## Sheet1
Section | Page | Status | Feature | Type | Chevron? | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Validation | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
App Type Selection | App Type | Dev and passed testing | Space Control | Radio Button | n | cfg/i/mainSequence | SpaceControlDemandSZVAV | [10 empty] | Aligned
|  | Dev and passed testing | Standard (Default) | Child Radio | y | cfg/i/spaceControl/mode | Eco | [10 empty] | Aligned
|  | Dev and passed testing | Precision | Child Radio | y | cfg/i/spaceControl/mode | Precision | [10 empty] | Aligned
|  | Dev and passed testing | VAV Control | Radio Button | y | cfg/i/mainSequence | SupplyAirControl | [10 empty] | Not Aligned
|  | Dev and passed testing | Outdoor Air Control | Radio Button | y | cfg/i/mainSequence | OutdoorAirControl | [10 empty] | Not for April
|  | Dev and passed testing | Has Return Air | Child Checkbox | y | pcfg/i/systemConfig/_/unitConfig/ahuProcess/hasReturnDucting | true/false
|  | Dev and failed testing | Return Air Control | Radio Button | y | cfg/i/mainSequence | SpaceControlDemandSZVAV | cfg/i/spaceControl/useReturnOverSpaceTemp | true/false
|  | Can't Test | 3rd Party Interface | Radio Button | y |  |  |  |  | Must Configure 3pi Board
|  | Dev and failed testing | Enable Unoccupied Setpoints | checkbox | y | cfg/i/unoccTempControlEnable | true/false | [10 empty] | Not Aligned
Space Control (Standard) | Standard | Dev and passed testing | Occupied Cooling Setpoint | Setpoint |  | sp/i/occCoolSpaceTempSP | integer | [5 empty] | F or C
|  | Dev and passed testing | Occupied Heating Setpoint | Setpoint |  | sp/i/occHeatSpaceTempSP | integer | [5 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Not Tested | Unoccupied Cooling Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | integer
|  | Not Tested | Unoccupied Heating Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | integer
Night Setback | Night Setback Unoccupied Temps | Not Tested | Unoccupied Cooling Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | integer | [5 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Not Tested | Unoccupied Heating Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | integer | [5 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
Space Control (Precision) | Precision Mode Type | Dev and passed testing | Manual (Default) | Radio Button | y | cfg/i/spaceControl/seasonChangeover/auto | false
|  | Dev and passed testing | Auto Season Changeover Enable | Radio Button | y | cfg/i/spaceControl/seasonChangeover/auto | true
| Manual Setpoints | Dev and passed testing | Occupied Space Temperature Setpoint | Setpoint |  | cfg/i/spaceControl/summerSP | integer | [5 empty] | F or C | -30 | 110 | 72 | This is the Mode Enable Setpoint that calls for Occupied Cooling Mode. When the HVAC mode enable source temperature is above this value will put the unit into cooling mode.
|  | Dev and passed testing | Unoccupied Cooling Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | integer | [5 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Dev and passed testing | Unoccupied Heating Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | integer | [5 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Dev and failed testing | High Tolerance | Setpoint |  | cfg/i/spaceControl/season | Winter OR Summer | pcfg/i/pid/winterDemand/_/accelerationBand/errorHigh and pcfg/i/pid/summerDemand/_/accelerationBand/errorHigh | Integer | Check to see if cfg/i/spaceControl/season is in summer or winter, then publish to the corresponding topic. if noting is received, default to summer. |  |  | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint |  | Subscribe to first topic to descide which second topic to use.
|  | Dev and failed testing | Low Tolerance | Setpoint |  | cfg/i/spaceControl/season | Winter OR Summer | pcfg/i/pid/winterDemand/_/accelerationBand/errorLow and pcfg/i/pid/summerDemand/_/accelerationBand/errorLow | Integer | Check to see if cfg/i/spaceControl/season is in summer or winter, then publish to the corresponding topic. if noting is received, default to summer. |  |  | F or C | [5 empty] | Subscribe to first topic to descide which second topic to use.
| Auto Season Setpoints 1 | Dev and passed testing | Occupied Summer Setpoint | Setpoint |  | cfg/i/spaceControl/summerSP | Integer | [5 empty] | F or C
|  | Dev and passed testing | Occupied Winter Setpoint | Setpoint |  | cfg/i/spaceControl/winterSP | Integer | [5 empty] | F or C | -30 | 110 | 72
|  | Dev and failed testing | Unoccupied Heating Winter Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | Integer | [5 empty] | F or C | -30 | 110 |  | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Dev and failed testing | Unoccupied Cooling Winter Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | Integer | [5 empty] | F or C | -30 | 110 |  | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
|  | Dev and failed testing | Unoccupied Heating Summer Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | Integer | [5 empty] | F or C | -30 | 110
|  | Dev and failed testing | Unoccupied Cooling Summer Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | Integer | [5 empty] | F or C | -30 | 110
| Auto Season Setpoints 2 | Dev and failed testing | High Tolerance | Setpoint |  | cfg/i/spaceControl/season | Winter OR Summer | pcfg/i/pid/winterDemand/_/accelerationBand/errorHigh and pcfg/i/pid/summerDemand/_/accelerationBand/errorHigh | Integer |  |  |  | F or C
|  | Dev and failed testing | Low Tolerance | Setpoint |  | cfg/i/spaceControl/season | Winter OR Summer | pcfg/i/pid/winterDemand/_/accelerationBand/errorLow and pcfg/i/pid/summerDemand/_/accelerationBand/errorLow | Integer |  |  |  | F or C | -30 | 110 | 74
|  | Dev and passed testing | Summer Outdoor Air Enable Setpoint | Setpoint |  | cfg/i/spaceControl/seasonChangeover/summerOATemp | [6 empty] | F or C | -30 | 110 | 70
|  | Dev and passed testing | Winter Outdoor Air Enable Setpoint | Setpoint |  | cfg/i/spaceControl/seasonChangeover/winterOATemp | [6 empty] | F or C | -30 | 110 | 75
|  | Dev and passed testing | Season Changeover Time | Setpoint |  | cfg/i/spaceControl/seasonChangeover/time | [6 empty] | Min | -30 | 110 | 55
|  | Dev and passed testing | Season Changeover Duration | Setpoint |  | cfg/i/spaceControl/seasonChangeover/successfulChecks/req | [6 empty] | Days
VAV Control | VAV - Config | Can't Test | Morning Warm Up | Checkbox | y | cfg/i/manager/morningWarmup/enabled | boolean
|  | Can't Test | Morning Cool Down | Checkbox | y | cfg/i/manager/morningCooldown/enabled | boolean
|  | Can't Test | Enable Unit Heating | Checkbox | y | cfg/i/manager/vav/heatingEnabled | boolean
| Morning Warmup SP's | Can't Test | Return Air Temp | Setpoint |  | cfg/i/manager/morningWarmup/raSetpoint | float (degrees F)
|  | Can't Test | Time Period | Setpoint |  | cfg/i/manager/morningWarmup/duration | integer (minutes)
|  | Can't Test | Supply Air Heating | Setpoint |  | cfg/i/manager/morningWarmup/supplyAirSetpoint | float (degrees F)
| Morning Cooldown SP's | Can't Test | Return Air Temp | Setpoint |  | cfg/i/manager/morningCooldown/raSetpoint | float (degrees F)
|  | Can't Test | Time Period | Setpoint |  | cfg/i/manager/morningCooldown/duration | integer (minutes)
|  | Can't Test | Supply Air Heating | Setpoint |  | cfg/i/manager/morningCooldown/supplyAirSetpoint | float (degrees F)
| Unit Heating SP's | Can't Test | Cool OAT Enable Setpoint | Setpoint |  | sp/i/occCoolSpaceTempSP | float (degrees F)
|  | Can't Test | Heat OAT Enable Setpoint | Setpoint |  | sp/i/occHeatSpaceTempSP | float (degrees F)
| Duct Static Pressure Setpoint | Can't Test | Duct Static Pressure Setpoint | Setpoint |  | sp/i/ductStaticPressureSP | float (wg)
| VAV - SAT Reset | Can't Test | No SAT Reset | Radio Button | n | cfg/i/manager/satReset/enable | boolean
|  | Can't Test | Enable SAT Reset | Radio Button | y | cfg/i/manager/satReset/enable | boolean
| VAV - SAT Source Type | Can't Test | Outside Air | Radio Button | y | cfg/i/manager/satReset/source | OA
|  | Can't Test | Space Air | Radio Button | y | cfg/i/manager/satReset/source | Space
|  | Can't Test | Return Air | Radio Button | y | cfg/i/manager/satReset/source | Return
|  | Can't Test | Supply Fan VFD | Radio Button | y | cfg/i/manager/satReset/source | SupplyFanSpeed
|  | Can't Test | Remote Voltage Signal | Radio Button | y | cfg/i/manager/satReset/source | RemoteVoltageSignal |  |  | Must Configure 3pi Board
| VAV - SAT SP's | Can't Test | Heat SAT Low | Setpoint |  | sp/i/saTempHeatSP/min | [10 empty] | This is the desired Supply Air Temperature to be maintained during the heating mode of operation. When Supply Air Reset Source has been configured, the SAT Heating Setpoint is adjusted down to this value as the reset source temperature rises to the SAT Heating High Reset Source Setpoint.
|  | Can't Test | Heat SAT High | Setpoint |  | sp/i/saTempHeatSP/max | [10 empty] | When the Supply Air Reset Source has been configured, the SAT Heating Setpoint is adjusted up to this value as the reset source temperature falls to the SAT Heating Low Reset Source Setpoint.
|  | Can't Test | Source Heat SAT Low | Setpoint |  | cfg/i/manager/satReset/source/heat/minValue | [10 empty] | As the reset source drops to this temperature, the supply air setpoint rises to what the ‘SAT High Reset Limit’ is set at.
|  | Can't Test | Source Heat SAT High | Setpoint |  | cfg/i/manager/satReset/source/heat/maxValue | [6 empty] | F or C | 0 | 250 |  | As the reset source rises to this temperature, the supply air setpoint drops to what the ‘SAT Setpoint or Low SAT Limit for Reset’ is set at.
|  | Can't Test | Cool SAT Low | Setpoint |  | sp/i/saTempCoolSP/min | [6 empty] | F or C | 0 | 100 | 55 | This is the desired Supply Air Temperature to be maintained during the cooling mode of operation. When supply air reset has been configured, the SAT Cooling Setpoint is adjusted down to this value as the reset source temperature rises to the SAT Cooling High Reset Source Setpoint.
|  | Can't Test | Cool SAT High | Setpoint |  | sp/i/saTempCoolSP/max | [6 empty] | F or C | 0 | 100 | 65 | When the Supply Air Reset Source is configured, the SAT Cooling Setpoint is adjusted up to this value as the reset source temperature falls to the SAT Cooling Low Reset Source Setpoint.
|  | Can't Test | Source Cool SAT Low | Setpoint |  | cfg/i/manager/satReset/source/cool/minValue | [6 empty] | F or C | -30 | 250 |  | As the reset source drops to this temperature, the supply air setpoint rises to what the ‘SAT High Reset Limit’ is set at.
|  | Can't Test | Source Cool SAT High | Setpoint |  | cfg/i/manager/satReset/source/cool/maxValue | [6 empty] | F or C | -30 | 250 |  | As the reset source rises to this temperature, the supply air setpoint drops to what the ‘SAT Setpoint or Low SAT Limit for Reset’ is set at.
| VAV - DDC SP's | Can't Test | Min Voltage | Setpoint |  | cfg/i/manager/satReset/source/minVolts
|  | Can't Test | Max Voltage | Setpoint |  | cfg/i/manager/satReset/source/maxVolts
|  | Can't Test | Min Volt Cooling Temperature | Setpoint |  | sp/i/saTempCoolSP/min
|  | Can't Test | Max Volt Cooling Temperature | Setpoint |  | sp/i/saTempCoolSP/max
|  | Can't Test | Min Volt Heating Temp | Setpoint |  | sp/i/saTempHeatSP/min
|  | Can't Test | Max Volt Heating Temperature | Setpoint |  | sp/i/saTempHeatSP/max
OA Control | OA Setpoints | Can't Test | Occupied Cooling Setpoint | Setpoint |  | sp/i/occCoolSpaceTempSP | [6 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Can't Test | Occupied Heating Setpoint | Setpoint |  | sp/i/occHeatSpaceTempSP | [6 empty] | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
| OA Control - SAT Reset | Can't Test | No SAT Reset | Radio Button | n | cfg/i/manager/satReset/enable | boolean
|  | Can't Test | Enable SAT Reset | Radio Button |  | cfg/i/manager/satReset/enable | boolean
|  | Can't Test | Outside Air | Radio Button |  | cfg/i/manager/satReset/source | OA
|  | Can't Test | Space Air | Radio Button |  | cfg/i/manager/satReset/source | Space
|  | Can't Test | Return Air Control | Radio Button |  | cfg/i/manager/satReset/source | Return
|  | Can't Test | Fan VFD | Radio Button |  | cfg/i/manager/satReset/source | SupplyFanSpeed
|  | Can't Test | Remote Voltage Signal | Radio Button |  | cfg/i/manager/satReset/source | RemoteVoltageSignal |  |  | Must Configure 3pi Board
| VAV - DDC SP's | Can't Test | Min Voltage | Setpoint |  | cfg/i/manager/satReset/source/minVolts
|  | Can't Test | Max Voltage | Setpoint |  | cfg/i/manager/satReset/source/maxVolts
|  | Can't Test | Min Volt Cooling Temperature | Setpoint |  | sp/i/saTempCoolSP/min
|  | Can't Test | Max Volt Cooling Temperature | Setpoint |  | sp/i/saTempCoolSP/max
|  | Can't Test | Min Volt Heating Temp | Setpoint |  | sp/i/saTempHeatSP/min
|  | Can't Test | Max Volt Heating Temperature | Setpoint |  | sp/i/saTempHeatSP/max
OA + Return Air Control | OA + RA Setpoints | Can't Test | Unoccupied Cooling Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | [6 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Can't Test | Unoccupied Heating Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | [6 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
3rd Party Interface | 3pi Type | Can't Test | Thermostat | Radio Button | n
|  | Can't Test | Heat Pump Thermostat | Radio Button | y
|  | Can't Test | DDC | Radio Button | y
| Heat Pump Thermostat Type | Can't Test | Fail to Heat | Radio Button | n
|  | Can't Test | Fail to Cool | Radio Button | n
| DDC Control Enables | Can't Test | Heat Wheel | Checkbox | n
|  | Can't Test | Supply Fan | Checkbox | y
|  | Can't Test | Return/Exhaust Fan | Checkbox | y | This hasn't been defined yet
|  | Can't Test | OA/Econ Damper | Checkbox | y
|  | Can't Test | SAT Reset | Checkbox | y
| DDC Supply Fan Setpoints | Can't Test | Min Voltage | Setpoint
|  | Can't Test | Max Voltage | Setpoint
| DDC Return/Exhaust Fan Setpoints | Can't Test | Min Voltage | Setpoint
|  | Can't Test | Max Voltage | Setpoint
| DDC OA/Econ Damper Setpoints | Can't Test | Min Voltage | Setpoint
|  | Can't Test | Max Voltage | Setpoint
| VAV - DDC SP's | Can't Test | Min Voltage | Setpoint
|  | Can't Test | Max Voltage | Setpoint
|  | Can't Test | Min Volt Cooling Temperature | Setpoint
|  | Can't Test | Max Volt Cooling Temperature | Setpoint
|  | Can't Test | Min Volt Heating Temp | Setpoint
|  | Can't Test | Max Volt Heating Temperature | Setpoint
Return Air Control | Return Air Setpoints | Can't Test | Occupied Cooling Setpoint | Setpoint |  | sp/i/occCoolSpaceTempSP | [6 empty] | F or C
|  | Can't Test | Unoccupied Cooling Setpoint | Setpoint |  | sp/i/occHeatSpaceTempSP | [6 empty] | F or C
|  | Can't Test | Occupied Heating Setpoint | Setpoint |  | sp/i/unoccCoolSpaceTempSP | [6 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Can't Test | Unoccupied Heating Setpoint | Setpoint |  | sp/i/unoccHeatSpaceTempSP | [6 empty] | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
Can't Test
Unknown
Can't Test
Scalings | Temp Scaling | Dev and failed testing | Fahrenheit (Default) | Radio Button | n | cfg/i/displayInCelcius | FALSE
|  | Dev and failed testing | Celcius | Radio Button | n | cfg/i/displayInCelcius | TRUE
| Pressure Scaling | Can't Test | PSI | Radio Button | n
|  | Can't Test | "WG | Radio Button | n
| Airflow Scaling | Can't Test | CFM | Radio Button | n
|  | Can't Test | l/s | Radio Button | n
Can't Test
Unknown
Can't Test
Daylight Savings | Daylight Savings Enable | Can't Test | Daylight Savings Schedule Enable | checkbox | y
| Daylight Savings SP's | Can't Test | Start Date | Date Selector
|  | Can't Test | End Date | Date Selector
Can't Test
Unknown
Can't Test
Simultaneous Heat/Cool | Simultaneous Heat/Cool | Can't Test | Disabled |  |  | cfg/i/manager/simulHeatCool
|  | Can't Test | Enabled |  |  | cfg/i/manager/simulHeatCool
Can't Test

## Unit Settings
Section | Page | Status | Feature | Type | Chevron? | QA Status | Dev Status | Topic | Payload | Retained Topic | Topic 2 (if required) | Payload 2 (if required) | Validation | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
App Type Selection | App Type | Dev and passed testing | Space Control | Radio Button | n | working |  | cfg/i/mainSequence | SpaceControlDemandSZVAV | [11 empty] | Aligned
|  | Dev and passed testing | Standard (Default) | Child Radio | y | working |  | cfg/i/spaceControl/mode | Eco | [11 empty] | Aligned
|  | Dev and passed testing | Precision | Child Radio | y | working |  | cfg/i/spaceControl/mode | Precision | [11 empty] | Aligned
|  | Dev and passed testing | VAV Control | Radio Button | y | working |  | cfg/i/mainSequence | SupplyAirControl | [11 empty] | Not Aligned
|  | Dev and passed testing | Outdoor Air Control | Radio Button | y | working |  | cfg/i/mainSequence | OutdoorAirControl | [11 empty] | Not for April
|  | Dev and passed testing | Has Return Air | Child Checkbox | y | working | Working | pcfg/i/systemConfig/_/unitConfig/ahuProcess/hasReturnDucting | true/false
|  | Dev and failed testing | Return Air Control | Radio Button | y | Not Working, it selects the space control |  | cfg/i/mainSequence | ReturnAirControl |  | cfg/i/spaceControl/useReturnOverSpaceTemp | true/false
|  | Can't Test | 3rd Party Interface | Radio Button | y | working |  | test/topic/third_party_interface | 3rdPartyInterface |  |  |  | Must Configure 3pi Board
|  | Dev and failed testing | Enable Unoccupied Setpoints | checkbox | y | working | working | cfg/i/unoccTempControlEnable | true/false | [11 empty] | Not Aligned
Space Control (Standard) | Standard | Dev and passed testing | Occupied Cooling Setpoint | Setpoint |  | working |  | sp/i/occCoolSpaceTempSP | integer | [6 empty] | F or C
|  | Dev and passed testing | Occupied Heating Setpoint | Setpoint |  | working |  | sp/i/occHeatSpaceTempSP | integer | [6 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Not Tested | Unoccupied Cooling Setpoint | Setpoint |  | working |  | sp/i/unoccCoolSpaceTempSP | integer
|  | Not Tested | Unoccupied Heating Setpoint | Setpoint |  | working |  | sp/i/unoccHeatSpaceTempSP | integer
Night Setback | Night Setback Unoccupied Temps | Not Tested | Unoccupied Cooling Setpoint | Setpoint |  | working |  | sp/i/unoccCoolSpaceTempSP | integer | [6 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Not Tested | Unoccupied Heating Setpoint | Setpoint |  | working |  | sp/i/unoccHeatSpaceTempSP | integer | [6 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
Space Control (Precision) | Precision Mode Type | Dev and passed testing | Manual (Default) | Radio Button | y | working |  | cfg/i/spaceControl/seasonChangeover/auto | false
|  | Dev and passed testing | Auto Season Changeover Enable | Radio Button | y | working |  | cfg/i/spaceControl/seasonChangeover/auto | true
| Manual Setpoints | Dev and passed testing | Occupied Space Temperature Setpoint | Setpoint |  | working |  | cfg/i/spaceControl/summerSP | integer | [6 empty] | F or C | -30 | 110 | 72 | This is the Mode Enable Setpoint that calls for Occupied Cooling Mode. When the HVAC mode enable source temperature is above this value will put the unit into cooling mode.
|  | Dev and passed testing | Unoccupied Cooling Setpoint | Setpoint |  | working |  | sp/i/unoccCoolSpaceTempSP | integer | [6 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Dev and passed testing | Unoccupied Heating Setpoint | Setpoint |  | working |  | sp/i/unoccHeatSpaceTempSP | integer | [6 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Dev and failed testing | High Tolerance | Setpoint |  | Not Working | Need clarification | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorHigh and pcfg/i/pid/summerDemand/_/accelerationBand/errorHigh | Integer | Check to see if cfg/i/spaceControl/season is in summer or winter, then publish to the corresponding topic. if noting is received, default to summer. |  |  | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint |  | Subscribe to first topic to descide which second topic to use.
|  | Dev and failed testing | Low Tolerance | Setpoint |  | Not Working | Need clarification | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorLow and pcfg/i/pid/summerDemand/_/accelerationBand/errorLow | Integer | Check to see if cfg/i/spaceControl/season is in summer or winter, then publish to the corresponding topic. if noting is received, default to summer. |  |  | F or C | [5 empty] | Subscribe to first topic to descide which second topic to use.
| Auto Season Setpoints 1 | Dev and passed testing | Occupied Summer Setpoint | Setpoint |  | working |  | cfg/i/spaceControl/summerSP | Integer | [6 empty] | F or C
|  | Dev and passed testing | Occupied Winter Setpoint | Setpoint |  | working |  | cfg/i/spaceControl/winterSP | Integer | [6 empty] | F or C | -30 | 110 | 72
|  | Dev and failed testing | Unoccupied Heating Winter Setpoint | Setpoint |  | Not Working | Need clarification since its same topic | sp/i/unoccHeatSpaceTempSP | Integer | [6 empty] | F or C | -30 | 110 |  | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Dev and failed testing | Unoccupied Cooling Winter Setpoint | Setpoint |  | Not Working | Need clarification since its same topic | sp/i/unoccCoolSpaceTempSP | Integer | [6 empty] | F or C | -30 | 110 |  | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
|  | Dev and failed testing | Unoccupied Heating Summer Setpoint | Setpoint |  | Not Working | Need clarification since its same topic | sp/i/unoccHeatSpaceTempSP | Integer | [6 empty] | F or C | -30 | 110
|  | Dev and failed testing | Unoccupied Cooling Summer Setpoint | Setpoint |  | Not Working | Need clarification since its same topic | sp/i/unoccCoolSpaceTempSP | Integer | [6 empty] | F or C | -30 | 110
| Auto Season Setpoints 2 | Dev and failed testing | High Tolerance | Setpoint |  | Not Working | Need clarification | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorHigh and pcfg/i/pid/summerDemand/_/accelerationBand/errorHigh | Integer |  |  |  | F or C
|  | Dev and failed testing | Low Tolerance | Setpoint |  | Not Working | Need clarification | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorLow and pcfg/i/pid/summerDemand/_/accelerationBand/errorLow | Integer |  |  |  | F or C | -30 | 110 | 74
|  | Dev and passed testing | Summer Outdoor Air Enable Setpoint | Setpoint |  | working |  | cfg/i/spaceControl/seasonChangeover/summerOATemp | [7 empty] | F or C | -30 | 110 | 70
|  | Dev and passed testing | Winter Outdoor Air Enable Setpoint | Setpoint |  | working |  | cfg/i/spaceControl/seasonChangeover/winterOATemp | [7 empty] | F or C | -30 | 110 | 75
|  | Dev and passed testing | Season Changeover Time | Setpoint |  | working |  | cfg/i/spaceControl/seasonChangeover/time | [7 empty] | Min | -30 | 110 | 55
|  | Dev and passed testing | Season Changeover Duration | Setpoint |  | working |  | cfg/i/spaceControl/seasonChangeover/successfulChecks/req | [7 empty] | Days
VAV Control | VAV - Config | Can't Test | Morning Warm Up | Checkbox | y | working |  | cfg/i/manager/morningWarmup/enabled | boolean
|  | Can't Test | Morning Cool Down | Checkbox | y | working |  | cfg/i/manager/morningCooldown/enabled | boolean
|  | Can't Test | Enable Unit Heating | Checkbox | y | working |  | cfg/i/manager/vav/heatingEnabled | boolean
| Morning Warmup SP's | Can't Test | Return Air Temp | Setpoint |  | working |  | cfg/i/manager/morningWarmup/raSetpoint | float (degrees F)
|  | Can't Test | Time Period | Setpoint |  | working |  | cfg/i/manager/morningWarmup/duration | integer (minutes)
|  | Can't Test | Supply Air Heating | Setpoint |  | working |  | cfg/i/manager/morningWarmup/supplyAirSetpoint | float (degrees F)
| Morning Cooldown SP's | Can't Test | Return Air Temp | Setpoint |  | working |  | cfg/i/manager/morningCooldown/raSetpoint | float (degrees F)
|  | Can't Test | Time Period | Setpoint |  | working |  | cfg/i/manager/morningCooldown/duration | integer (minutes)
|  | Can't Test | Supply Air Heating | Setpoint |  | working |  | cfg/i/manager/morningCooldown/supplyAirSetpoint | float (degrees F)
| Unit Heating SP's | Can't Test | Cool OAT Enable Setpoint | Setpoint |  | Not Working | working | sp/i/occCoolSpaceTempSP | float (degrees F)
|  | Can't Test | Heat OAT Enable Setpoint | Setpoint |  | Not Working The Heat Setpoint is linked to the Cool Setpoint | working | sp/i/occHeatSpaceTempSP | float (degrees F)
| Duct Static Pressure Setpoint | Can't Test | Duct Static Pressure Setpoint | Setpoint |  | working |  | sp/i/ductStaticPressureSP | float (wg)
| VAV - SAT Reset | Can't Test | No SAT Reset | Radio Button | n | working | working | cfg/i/manager/satReset/enable | boolean
|  | Can't Test | Enable SAT Reset | Radio Button | y | working | working | cfg/i/manager/satReset/enable | boolean
| VAV - SAT Source Type | Can't Test | Outside Air | Radio Button | y | working | working | cfg/i/manager/satReset/source | OA
|  | Can't Test | Space Air | Radio Button | y | working | working | cfg/i/manager/satReset/source | Space
|  | Can't Test | Return Air | Radio Button | y | working | working | cfg/i/manager/satReset/source | Return
|  | Can't Test | Supply Fan VFD | Radio Button | y | working | working | cfg/i/manager/satReset/source | SupplyFanSpeed
|  | Can't Test | Remote Voltage Signal | Radio Button | y | working | working | cfg/i/manager/satReset/source | RemoteVoltageSignal |  |  |  | Must Configure 3pi Board
| VAV - SAT SP's | Can't Test | Heat SAT Low | Setpoint |  | working |  | sp/i/saTempHeatSP/min | [11 empty] | This is the desired Supply Air Temperature to be maintained during the heating mode of operation. When Supply Air Reset Source has been configured, the SAT Heating Setpoint is adjusted down to this value as the reset source temperature rises to the SAT Heating High Reset Source Setpoint.
|  | Can't Test | Heat SAT High | Setpoint |  | working |  | sp/i/saTempHeatSP/max | [11 empty] | When the Supply Air Reset Source has been configured, the SAT Heating Setpoint is adjusted up to this value as the reset source temperature falls to the SAT Heating Low Reset Source Setpoint.
|  | Can't Test | Source Heat SAT Low | Setpoint |  | working | working | cfg/i/manager/satReset/source/heat/minValue | [11 empty] | As the reset source drops to this temperature, the supply air setpoint rises to what the ‘SAT High Reset Limit’ is set at.
|  | Can't Test | Source Heat SAT High | Setpoint |  | working | working | cfg/i/manager/satReset/source/heat/maxValue | [7 empty] | F or C | 0 | 250 |  | As the reset source rises to this temperature, the supply air setpoint drops to what the ‘SAT Setpoint or Low SAT Limit for Reset’ is set at.
|  | Can't Test | Cool SAT Low | Setpoint |  | working |  | sp/i/saTempCoolSP/min |  | Retained | [5 empty] | F or C | 0 | 100 | 55 | This is the desired Supply Air Temperature to be maintained during the cooling mode of operation. When supply air reset has been configured, the SAT Cooling Setpoint is adjusted down to this value as the reset source temperature rises to the SAT Cooling High Reset Source Setpoint.
|  | Can't Test | Cool SAT High | Setpoint |  | working |  | sp/i/saTempCoolSP/max |  | Retained | [5 empty] | F or C | 0 | 100 | 65 | When the Supply Air Reset Source is configured, the SAT Cooling Setpoint is adjusted up to this value as the reset source temperature falls to the SAT Cooling Low Reset Source Setpoint.
|  | Can't Test | Source Cool SAT Low | Setpoint |  | working | working | cfg/i/manager/satReset/source/cool/minValue |  | Retained | [5 empty] | F or C | -30 | 250 |  | As the reset source drops to this temperature, the supply air setpoint rises to what the ‘SAT High Reset Limit’ is set at.
|  | Can't Test | Source Cool SAT High | Setpoint |  | working | working | cfg/i/manager/satReset/source/cool/maxValue |  | Retained | [5 empty] | F or C | -30 | 250 |  | As the reset source rises to this temperature, the supply air setpoint drops to what the ‘SAT Setpoint or Low SAT Limit for Reset’ is set at.
| VAV - DDC SP's | Can't Test | Min Voltage | Setpoint |  | working | working | cfg/i/manager/satReset/source/minVolts
|  | Can't Test | Max Voltage | Setpoint |  | working | working | cfg/i/manager/satReset/source/maxVolts
|  | Can't Test | Min Volt Cooling Temperature | Setpoint |  | working | working | sp/i/saTempCoolSP/min
|  | Can't Test | Max Volt Cooling Temperature | Setpoint |  | working | working | sp/i/saTempCoolSP/max
|  | Can't Test | Min Volt Heating Temp | Setpoint |  | working | working | sp/i/saTempHeatSP/min
|  | Can't Test | Max Volt Heating Temperature | Setpoint |  | working | working | sp/i/saTempHeatSP/max
OA Control | OA Setpoints | Can't Test | Occupied Cooling Setpoint | Setpoint |  | working |  | sp/i/occCoolSpaceTempSP | [7 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Can't Test | Occupied Heating Setpoint | Setpoint |  | working |  | sp/i/occHeatSpaceTempSP | [7 empty] | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
| OA Control - SAT Reset | Can't Test | No SAT Reset | Radio Button | n | working | working | cfg/i/manager/satReset/enable | boolean
|  | Can't Test | Enable SAT Reset | Radio Button |  | working | working | cfg/i/manager/satReset/enable | boolean
|  | Can't Test | Outside Air | Radio Button |  | working | working | cfg/i/manager/satReset/source | OA
|  | Can't Test | Space Air | Radio Button |  | working | working | cfg/i/manager/satReset/source | Space
|  | Can't Test | Return Air Control | Radio Button |  | working | working | cfg/i/manager/satReset/source | Return
|  | Can't Test | Fan VFD | Radio Button |  | working | working | cfg/i/manager/satReset/source | SupplyFanSpeed
|  | Can't Test | Remote Voltage Signal | Radio Button |  | working | working | cfg/i/manager/satReset/source | RemoteVoltageSignal |  |  |  | Must Configure 3pi Board
| VAV - DDC SP's | Can't Test | Min Voltage | Setpoint |  | working | working | cfg/i/manager/satReset/source/minVolts
|  | Can't Test | Max Voltage | Setpoint |  | working | working | cfg/i/manager/satReset/source/maxVolts
|  | Can't Test | Min Volt Cooling Temperature | Setpoint |  | working | working | sp/i/saTempCoolSP/min
|  | Can't Test | Max Volt Cooling Temperature | Setpoint |  | working | working | sp/i/saTempCoolSP/max
|  | Can't Test | Min Volt Heating Temp | Setpoint |  | working | working | sp/i/saTempHeatSP/min
|  | Can't Test | Max Volt Heating Temperature | Setpoint |  | working | working | sp/i/saTempHeatSP/max
OA + Return Air Control | OA + RA Setpoints | Can't Test | Unoccupied Cooling Setpoint | Setpoint |  | working |  | sp/i/unoccCoolSpaceTempSP | [7 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Can't Test | Unoccupied Heating Setpoint | Setpoint |  | working |  | sp/i/unoccHeatSpaceTempSP | [7 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
3rd Party Interface | 3pi Type | Can't Test | Thermostat | Radio Button | n | It’s working even without a payload | Working | test/topic/thermostat | Thermostat
|  | Can't Test | Heat Pump Thermostat | Radio Button | y | It’s working even without a payload | Working | test/topic/heat_pump_thermostat | HeatPumpThermostat
|  | Can't Test | DDC | Radio Button | y | It’s working even without a payload | Working | test/topic/ddc | DDC
| Heat Pump Thermostat Type | Can't Test | Fail to Heat | Radio Button | n | It’s working even without a payload | Working | test/topic/fail_to_heat | FailToHeat
|  | Can't Test | Fail to Cool | Radio Button | n | It’s working even without a payload | Working | test/topic/fail_to_cool | FailToCool
| DDC Control Enables | Can't Test | Heat Wheel | Checkbox | n | It’s working even without a payload | Working | test/topic/heat_wheel | HeatWheel
|  | Can't Test | Supply Fan | Checkbox | y | It’s working even without a payload | Working | test/topic/ddc_supply_fan | SupplyFan
|  | Can't Test | Return/Exhaust Fan | Checkbox | y | It’s working even without a payload | Working | test/topic/retun_or_exhaust_fan | Return/Exhaust Fan
|  | Can't Test | OA/Econ Damper | Checkbox | y | It’s working even without a payload | Working | test/topic/oa_or_econ_damper | OA/Econ Damper
|  | Can't Test | SAT Reset | Checkbox | y | It’s working even without a payload | Working | test/topic/sat_reset | SAT Reset
| DDC Supply Fan Setpoints | Can't Test | Min Voltage | Setpoint |  | Working | Working | test/topic/test_supp_min_voltage
|  | Can't Test | Max Voltage | Setpoint |  | Working | Working | test/topic/test_supp_max_voltage
| DDC Return/Exhaust Fan Setpoints | Can't Test | Min Voltage | Setpoint |  | Working | Working | test/topic/test_exh_min_voltage
|  | Can't Test | Max Voltage | Setpoint |  | Working | Working | test/topic/test_exh_max_voltage
| DDC OA/Econ Damper Setpoints | Can't Test | Min Voltage | Setpoint |  | Working | Working | test/topic/test_econ_min_voltage
|  | Can't Test | Max Voltage | Setpoint |  | Working | Working | test/topic/test_econ_max_voltage
| VAV - DDC SP's | Can't Test | Min Voltage | Setpoint |  | Working | Working | test/topic/test_sat_min_voltage
|  | Can't Test | Max Voltage | Setpoint |  | Working | Working | test/topic/test_sat_max_voltage
|  | Can't Test | Min Volt Cooling Temperature | Setpoint |  | Working | Working | test/topic/min_sat_volt_cooling_temp
|  | Can't Test | Max Volt Cooling Temperature | Setpoint |  | Working | Working | test/topic/max_sat_volt_cooling_temp
|  | Can't Test | Min Volt Heating Temp | Setpoint |  | Working | Working | test/topic/min_sat_volt_heating_temp
|  | Can't Test | Max Volt Heating Temperature | Setpoint |  | Working | Working | test/topic/max_sat_volt_heating_temp
Return Air Control | Return Air Setpoints | Can't Test | Occupied Cooling Setpoint | Setpoint |  | Working |  | sp/i/occCoolSpaceTempSP | [7 empty] | F or C
|  | Can't Test | Unoccupied Cooling Setpoint | Setpoint |  | Unoccupied Cooling Setpoint topic is linked to the Occupied Heating Setpoint |  | sp/i/occHeatSpaceTempSP | [7 empty] | F or C
|  | Can't Test | Occupied Heating Setpoint | Setpoint |  | Occupied Heating Setpoint topic is linked to Unoccupied Cooling SP |  | sp/i/unoccCoolSpaceTempSP | [7 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Can't Test | Unoccupied Heating Setpoint | Setpoint |  | Working |  | sp/i/unoccHeatSpaceTempSP | [7 empty] | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
Can't Test
Unknown
Can't Test
Scalings | Temp Scaling | Dev and failed testing | Fahrenheit (Default) | Radio Button | n | Working |  | cfg/i/displayInCelcius | false
|  | Dev and failed testing | Celcius | Radio Button | n | Working | Working | cfg/i/displayInCelcius | true
| Pressure Scaling | Can't Test | PSI | Radio Button | n
|  | Can't Test | "WG | Radio Button | n
| Airflow Scaling | Can't Test | CFM | Radio Button | n
|  | Can't Test | l/s | Radio Button | n
Can't Test
Unknown
Can't Test
Daylight Savings | Daylight Savings Enable | Can't Test | Daylight Savings Schedule Enable | checkbox | y
| Daylight Savings SP's | Can't Test | Start Date | Date Selector
|  | Can't Test | End Date | Date Selector
Can't Test
Unknown
Can't Test
Simultaneous Heat/Cool | Simultaneous Heat/Cool | Can't Test | Disabled |  |  | Working |  | cfg/i/manager/simulHeatCool
|  | Can't Test | Enabled |  |  | Working |  | cfg/i/manager/simulHeatCool
Can't Test

## Unit Settings - Boards
Section | Page | State | Feature | Type | Chevron? | Topic Notes | QA Status | Dev Status | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Boards | Type | Can't Test | Unit Manager | Checkbox | y |  |  |  | test/topic/boards_unit_manager | boolean
|  | Dev and failed testing | Power-Comm Board | Checkbox | y |  |  |  | ui/config/boardSelection/powerComm | boolean
|  | Dev and failed testing | Air Handler Board | Checkbox | y |  |  |  | ui/config/boardSelection/ahu | boolean
|  | Dev and failed testing | Cooling Board | Checkbox | y |  |  |  | ui/config/boardSelection/cooling | boolean
|  | Dev and failed testing | Heating Board | Checkbox | y |  |  |  | ui/config/boardSelection/heating | boolean
|  | Dev and failed testing | Energy Recovery Board | Checkbox | y |  |  |  | ui/config/boardSelection/energyRecovery | boolean
|  | Dev and failed testing | Preheat Board | Checkbox | y |  |  |  | ui/config/boardSelection/preheat | boolean
|  | Dev and failed testing | Outside Air Board | Checkbox | y |  |  |  | ui/config/boardSelection/outsideAir | boolean
Can't Test
Unit Manager |  | Unknown
Can't Test
Unit Manager | Unit Manager - BACnet | Not Developed | MS/TP | Radio Button | y |  | Working |  | cfg/i/gc/bacnetConfig/protocol | mstp
|  | Not Developed | IP | Radio Button | y |  | Working |  | cfg/i/gc/bacnetConfig/protocol | ip
| BACnet MS/TP - Baud Rate | Not Developed | 4800 | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 4800
|  | Not Developed | 9600 | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 9600
|  | Not Developed | 19200 | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 19200
|  | Not Developed | 38400 | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 38400
|  | Not Developed | 57600 | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 57600
|  | Not Developed | 115200 | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 115200
| BACnet MS/TP - MAC Address | Not Developed | MAC Address | Setpoint | n |  | Working |  | cfg/i/gc/bacnetConfig/mstp/macAddress | {{int}}
| BACnet MS/TP - Device ID | Not Developed | Device ID | Setpoint | n |  | Working |  | cfg/i/gc/bacnetConfig/deviceID | {{int}}
| BACnet IP - Device ID | Not Developed | Device ID | Setpoint | n |  | Working |  | cfg/i/gc/bacnetConfig/deviceID | {{int}}
| BACnet IP - BBMD - Foreign Device Enabled | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/enable | false
|  | Not Developed | Enabled | Radio Button | y |  | Working |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/enable | true
| BACnet IP - BBMD - Network | Not Developed | BBMD IPv4 Address | Setpoint |  |  | Working |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/BBMDIP | 192.168.100.100
|  | Not Developed | Network Port | Setpoint |  |  | Working |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/BBMDPort | {{int}}
| Unit Manager - Network | Not Developed | DHCP - Auto | Toggle |  | Stratus/IP is only for status | Working |  | Stratus/IP | { "dhcp": true, "dns": [ "10.60.0.95", "10.60.0.96" ], "gateway": "10.60.100.1", "ip": "10.60.100.76", "mac": "6C:DF:FB:60:89:68", "netmask": 23 } | Stratus/IPConfigChange | { "dhcp": false, "dns": [ ], "gateway": "192.168.1.1", "ip": "192.168.1.102", "netmask": 24 }
|  | Not Developed | DHCP - Static | Toggle |  |  | Working |  | Stratus/IP |  | Stratus/IPConfigChange
|  | Not Developed | IPv4 | Setpoint |  |  | Working |  | Stratus/IP |  | Stratus/IPConfigChange
|  | Not Developed | Netmask | Setpoint |  |  | Working |  | Stratus/IP |  | Stratus/IPConfigChange
|  | Not Developed | Gateway Address | Setpoint |  |  | Working |  | Stratus/IP |  | Stratus/IPConfigChange
|  | Not Developed | DNS Server Address (optional) | Setpoint |  |  | Working |  | Stratus/IP |  | Stratus/IPConfigChange
|  | Not Developed | MAC Address | Status |  |  | Working |  | Stratus/IP |  | Stratus/IPConfigChange
|  | Not Developed | Ethernet | Status |  |  | Working |  | Stratus/IP
| Unit Manager - EBUS | Not Developed | Low Speed | Radio Button | n |  | Working |  | test/topic/unit_manager_ebus_selection | low
|  | Not Developed | High Speed | Radio Button | n |  | Working |  | test/topic/unit_manager_ebus_selection | high
Can't Test
Preheat Board |  | Unknown
Can't Test
Preheat Board | Count | Not Developed | 1 Board | Radio Button | n |  | Working |  | cfg/i/gc/boardCount/preheat | 1
|  | Not Developed | 2 Boards | Radio Button | n |  | Working |  | cfg/i/gc/boardCount/preheat | 2
Board 1 | Preheat Board 1 | Not Developed | Unique ID | Radio Button or Status | s |  | Working |  | cfg/i/gc/boards/preheat/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
Board 1 Temps | Temp 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/1/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/1/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/1/selection | preheatLeavingAirTemp
| Temp 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/2/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/2/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/2/selection | preheatLeavingAirTemp
| Temp 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/3/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/3/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/3/selection | preheatLeavingAirTemp
| Temp 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/4/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/4/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/4/selection | preheatLeavingAirTemp
| Temp 5 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/5/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/5/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/5/selection | preheatLeavingAirTemp
| Temp 6 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/6/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/6/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/6/selection | preheatLeavingAirTemp
| Temp 7 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/7/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/7/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/7/selection | preheatLeavingAirTemp
| Temp 8 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/8/selection | none
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/8/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/THERM/8/selection | preheatLeavingAirTemp
Board 1 Mouts | Mout 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | BACnetPassthrough
Not Developed
Board 2 | Preheat Board 2 | Not Developed | Unique ID | Radio Button or Status | n |  | Working |  | cfg/i/gc/boards/preheat/2/uuid |  | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
Board 2 Temps | Temp 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/1/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/1/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/1/selection
| Temp 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/2/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/2/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/2/selection
| Temp 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/3/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/3/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/3/selection
| Temp 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/4/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/4/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/4/selection
| Temp 5 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/5/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/5/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/5/selection
| Temp 6 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/6/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/6/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/6/selection
| Temp 7 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/7/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/7/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/7/selection
| Temp 8 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/8/selection
|  | Not Developed | Entering Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/8/selection
|  | Not Developed | Leaving Air | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/THERM/8/selection
Board 2 Mouts | Mout 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | none
|  | Not Developed | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | heatEnable
|  | Not Developed | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | BACnetPassthrough
Can't Test
Can't Test
Outside Air Board |  | Unknown
Can't Test
Outside Air Board | Count | Not Developed | 1 Board | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/outsideAir | 1
|  | Not Developed | 2 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/outsideAir | 2
| Board 1 | Not Developed | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/outsideAir/1/uuid |  | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Dampers | Not Developed | Damper 1 | Checkbox | y | This is a weird way of doing this, these will technically set the 'selection' of the damper to none when unchecked, but don't do anything when they are checked. Everywhere else we've had a radio option for 'none' rather than doing it this way | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | none
|  | Not Developed | Damper 2 | Checkbox | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | none
|  | Not Developed | Damper 3 | Checkbox | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | none
| Damper 1 Type | Not Developed | Outside Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | oaDamper
|  | Not Developed | Return Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | raDamper
|  | Not Developed | Return Air Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | rabDamper
|  | Not Developed | Exhaust Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | motorizedExhaustDamper
|  | Not Developed | Energy Recovery Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | erSupplyDamper
| Outside Air End Switch | Not Developed | Disabled | Radio Button | n | End switch is linked to the damper connector's location, not what type it is | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Return Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Return Air Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Damper 2 Type | Not Developed | Outside Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | oaDamper
|  | Not Developed | Return Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | raDamper
|  | Not Developed | Return Air Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | rabDamper
|  | Not Developed | Exhaust Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | motorizedExhaustDamper
|  | Not Developed | Energy Recovery Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | erSupplyDamper
| Outside Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Return Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Return Air Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Damper 3 Type | Not Developed | Outside Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | oaDamper
|  | Not Developed | Return Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | raDamper
|  | Not Developed | Return Air Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | rabDamper
|  | Not Developed | Exhaust Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | motorizedExhaustDamper
|  | Not Developed | Energy Recovery Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | erSupplyDamper
| Outside Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Return Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Return Air Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Binary Input 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | dirtyPreFilterSwitch
| Binary Input 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | dirtyPreFilterSwitch
| Binary Input 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | dirtyPreFilterSwitch
| Binary Input 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | dirtyPreFilterSwitch
| Analog Inputs | Not Developed | Outside Air Temp Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/1/selection | boolean
|  | Not Developed | Return Air Temp Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/2/selection | boolean
|  | Not Developed | Building Pressure Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/3/selection | boolean
|  | Not Developed | Exhaust Duct Static Pressure Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/4/selection | boolean
| Board 2 | Not Developed | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/outsideAir/2/uuid |  | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Dampers | Not Developed | Damper 1 | Checkbox | y | This is a weird way of doing this, these will technically set the 'selection' of the damper to none when unchecked, but don't do anything when they are checked. Everywhere else we've had a radio option for 'none' rather than doing it this way | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | none
|  | Not Developed | Damper 2 | Checkbox | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | none
|  | Not Developed | Damper 3 | Checkbox | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection | none
| Damper 1 Type | Not Developed | Outside Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | oaDamper
|  | Not Developed | Return Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | raDamper
|  | Not Developed | Return Air Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | rabDamper
|  | Not Developed | Exhaust Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | motorizedExhaustDamper
|  | Not Developed | Energy Recovery Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | erSupplyDamper
| Outside Air End Switch | Not Developed | Disabled | Radio Button | n | End switch is linked to the damper connector's location, not what type it is | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Return Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Return Air Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Damper 2 Type | Not Developed | Outside Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | oaDamper
|  | Not Developed | Return Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | raDamper
|  | Not Developed | Return Air Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | rabDamper
|  | Not Developed | Exhaust Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | motorizedExhaustDamper
|  | Not Developed | Energy Recovery Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | erSupplyDamper
| Outside Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Return Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Return Air Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Damper 3 Type | Not Developed | Outside Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Not Developed | Return Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Not Developed | Return Air Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Not Developed | Exhaust Air | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Not Developed | Energy Recovery Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
| Outside Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Return Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Return Air Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Exhaust Air End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Energy Recovery Bypass End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Binary Input 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | dirtyPreFilterSwitch
| Binary Input 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | dirtyPreFilterSwitch
| Binary Input 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | dirtyPreFilterSwitch
| Binary Input 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | none
|  | Not Developed | Supply Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | supplyAirflowSwitch
|  | Not Developed | Return Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | returnAirflowSwitch
|  | Not Developed | Exhaust Airflow Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | exhaustAirflowSwitch
|  | Not Developed | Dirty Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | dirtyFilterSwitch
|  | Not Developed | Dirty Pre-Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | dirtyPreFilterSwitch
| Analog Inputs | Not Developed | Outside Air Temp Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/1/selection | boolean
|  | Not Developed | Return Air Temp Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/2/selection | boolean
|  | Not Developed | Building Pressure Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/3/selection | boolean
|  | Not Developed | Exhaust Duct Static Pressure Enable | Checkbox | n |  | Working |  | cfg/i/gc/boards/outsideAir/1/AIN/4/selection | boolean
Can't Test
Heating Board |  | Unknown
Can't Test
Heating Board | Count | Dev and failed testing | 1 Board | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/heating | 1
|  | Dev and failed testing | 2 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/heating | 2
| Board 1 | Dev and failed testing | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/heating/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/1/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/1/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/2/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/2/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/2/selection | BACnetPassthrough
| Binary Input 3 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/3/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/3/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/3/selection | BACnetPassthrough
| Binary Input 4 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/4/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/4/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/4/selection | BACnetPassthrough
| Binary Input 5 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/5/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/5/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/BIN/5/selection | BACnetPassthrough
| Mout 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | none | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | inducerFanLowSpeed | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | none | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | heatEnable | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | BACnetPassthrough | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
| Mout 8 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | BACnetPassthrough
| Mod Gas Valve 1 | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/ModGasValve/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/ModGasValve/1/selection | modGasValve
| Mod Gas Valve 2 | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/ModGasValve/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/ModGasValve/2/selection | modGasValve
| Board 2 | Dev and failed testing | Unique ID | Status |  |  | Working |  | cfg/i/gc/boards/heating/2/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/1/selection | none | [12 empty] | IF Valve is configred as "Enabled" please gray out and default to "ignition proof", if it is made "disabled" default to "not used" and degray the box
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/1/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/2/selection | none | [12 empty] | IF Valve is configred as "Enabled" please gray out and default to "ignition proof", if it is made "disabled" default to "not used" and degray the box
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/2/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/2/selection | BACnetPassthrough
| Binary Input 3 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/3/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/3/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/3/selection | BACnetPassthrough
| Binary Input 4 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/4/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/4/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/4/selection | BACnetPassthrough
| Binary Input 5 - Gas Ignition Feedback | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/5/selection | none
|  | Dev and passed testing | Ignition Proof | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/5/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/BIN/5/selection | BACnetPassthrough
| Mout 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | inducerFanLowSpeed | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | heatEnable | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | none | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | heatEnable | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | BACnetPassthrough | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
| Mout 7 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | scrSignal
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Dev and passed testing | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | none
|  | Dev and passed testing | SCR Signal | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | scrSignal | [12 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | BACnetPassthrough
| Mod Gas Valve 1 | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/ModGasValve/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/ModGasValve/1/selection | modGasValve | [9 empty] | x
| Mod Gas Valve 2 | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/ModGasValve/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/2/ModGasValve/2/selection | modGasValve | [9 empty] | x
Can't Test
Energy Recovery Board |  | Unknown
Can't Test
Energy Recovery Board | Count | Not Developed | 1 Board | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/heatWheel | 1
|  | Not Developed | 2 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/heatWheel | 2
| Board 1 | Not Developed | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Thermistor 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/1/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/1/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/1/selection | erExhaustLeavingAirTemp
| Thermistor 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 3 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 4 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/3/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/3/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/3/selection | erExhaustLeavingAirTemp
| Thermistor 5 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/4/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/4/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/4/selection | erExhaustLeavingAirTemp
| Thermistor 6 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/5/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/5/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/THERM/5/selection | erExhaustLeavingAirTemp
| Binary Input 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | none
|  | Not Developed | Intake Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | rotationStatus
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | none
|  | Not Developed | Intake Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | rotationStatus
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | BACnetPassthrough
| Bypass 1 | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | none
|  | Not Developed | Supply Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | erSupplyDamper
|  | Not Developed | Exhaust Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | erExhaustDamper
|  | Not Developed | Single Supply/Exhaust Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | erSingleSupplyExhaustDamper
| Bypass 2 | Not Developed | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | none
|  | Not Developed | Supply Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | erSupplyDamper
|  | Not Developed | Exhaust Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | erExhaustDamper
|  | Not Developed | Single Supply/Exhaust Bypass | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | erSingleSupplyExhaustDamper
| Bypass 1 End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/endSwitch | true
| Bypass 2 End Switch | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/endSwitch | true
| VFD | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | none
|  | Not Developed | Enabled | Radio Button | y | needs chevron to VFD flow | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | heatWheel
| VFD | Not Developed | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | none
|  | Not Developed | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | heatWheel
| Heat Wheel Overload Input | Not Developed | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/overloadInput | none
|  | Not Developed | Overload Input 1 | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/overloadInput | overload1
|  | Not Developed | Overload Input 2 | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/overloadInput | overload2
| Supply Fan Type | Not Developed | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/vfdPortType | none
|  | Not Developed | Communicating | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/vfdPortType | commFan
|  | Not Developed | 0-10 | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Not Developed | Min Voltage | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/analogMinVolts | {{float}}
|  | Not Developed | Max Voltage | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/analogMaxVolts | {{float}}
| Motor Type | Not Developed | Electromagnet Motor (EM) | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/isPMM | false
|  | Not Developed | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/isPMM | true
| Electromagnet Motor Rating | Not Developed | Motor HP | Setpoint |  | This data is tied to the VFD port, make sure the PinLocation is in the topic correctly for all motor data entries | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/HP
|  | Not Developed | Motor RPM | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/serviceFactor
|  | Not Developed | Motor FLA | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/FLA
|  | Not Developed | Drive Min Frequency | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Not Developed | Motor HP | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/HP
|  | Not Developed | Motor RPM | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/serviceFactor
|  | Not Developed | Motor FLA | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/FLA
|  | Not Developed | Drive Min Frequency | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/nameplateFreq
|  | Not Developed | Ld | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.Ld
|  | Not Developed | Lq | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.Lq
|  | Not Developed | BEMF | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.BEMF
|  | Not Developed | Rs | Setpoint |  |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.Rs
| Voltage | Not Developed | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 0
|  | Not Developed | 208 vac | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 208
|  | Not Developed | 230 vac | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 230
|  | Not Developed | 460 vac | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 460
|  | Not Developed | 575 vac | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 575
| Mout 1 | Not Developed | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | none
|  | Not Developed | Heat Wheel Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | heatWheelEnable
|  | Not Developed | Heat Wheel Low Speed | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | heatWheelLowSpeed
|  | Not Developed | Bypass Damper Enable | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | bypassDamperEnable
|  | Not Developed | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | BACnetPassthrough
| Board 2 | Not Developed | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/heatWheel/2/uuid | {{int}}
| Thermistor 1 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/1/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/1/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/1/selection | erExhaustLeavingAirTemp
| Thermistor 2 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 3 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 4 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/3/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/3/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/3/selection | erExhaustLeavingAirTemp
| Thermistor 5 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/4/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/4/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/4/selection | erExhaustLeavingAirTemp
| Thermistor 6 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/5/selection | none
|  | Not Developed | Intake Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/5/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/5/selection | erExhaustLeavingAirTemp
| Binary Input 1 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | none
|  | Not Developed | Intake Filter Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | rotationStatus
|  | Not Developed | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | none
|  | Not Developed | Intake Filter Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | rotationStatus
|  | Not Developed | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | BACnetPassthrough
| Bypass 1 | Not Developed | Disabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/selection | none
|  | Not Developed | Enabled | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/selection | erSupplyDamper
| Bypass 2 | Not Developed | Disabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/selection | none
|  | Not Developed | Enabled | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/selection | erReturnDamper
| Bypass 1 End Switch | Not Developed | Disabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/endSwitch | true
| Bypass 2 End Switch | Not Developed | Disabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/endSwitch | true
| VFD | Not Developed | Disabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/1/selection | none
|  | Not Developed | Enabled | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/1/selection | heatWheel
| Heat Wheel Overload Input | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/overloadInput | none
|  | Not Developed | Overload Input 1 | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/overloadInput | overload1
|  | Not Developed | Overload Input 2 | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/overloadInput | overload2
| Supply Fan Type | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/vfdPortType | none
|  | Not Developed | Communicating | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/vfdPortType | commFan
|  | Not Developed | 0-10 | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Not Developed | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/analogMinVolts | {{float}}
|  | Not Developed | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/analogMaxVolts | {{float}}
| Motor Type | Not Developed | Electromagnet Motor (EM) | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/isPMM | false
|  | Not Developed | Permanent Magnet Motor (PMM) | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/isPMM | true
| Electromagnet Motor Rating | Not Developed | Motor HP | Setpoint |  | This data is tied to the VFD port, make sure the PinLocation is in the topic correctly for all motor data entries |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/HP
|  | Not Developed | Motor RPM | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/serviceFactor
|  | Not Developed | Motor FLA | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/FLA
|  | Not Developed | Drive Min Frequency | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Not Developed | Motor HP | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/HP
|  | Not Developed | Motor RPM | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/serviceFactor
|  | Not Developed | Motor FLA | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/FLA
|  | Not Developed | Drive Min Frequency | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/nameplateFreq
|  | Not Developed | Ld | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.Ld
|  | Not Developed | Lq | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.Lq
|  | Not Developed | BEMF | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.BEMF
|  | Not Developed | Rs | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.Rs
| Voltage | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 0
|  | Not Developed | 208 vac | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 208
|  | Not Developed | 230 vac | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 230
|  | Not Developed | 460 vac | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 460
|  | Not Developed | 575 vac | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 575
| Mout 1 | Not Developed | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | none
|  | Not Developed | Heat Wheel Enable | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | heatWheelEnable
|  | Not Developed | Heat Wheel Low Speed | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | heatWheelLowSpeed
|  | Not Developed | Bypass Damper Enable | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | bypassDamperEnable
|  | Not Developed | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | BACnetPassthrough
Can't Test
Can't Test
Power-Comm Board |  | Unknown
Can't Test
Power-Comm Board | Count | Dev and failed testing | 1 Board | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/powerComm | 1
|  | Dev and failed testing | 2 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/powerComm | 2
|  | Dev and failed testing | 3 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/powerComm | 3
|  | Dev and failed testing | 4 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/powerComm | 4
|  | Dev and failed testing | 5 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/powerComm | 5
|  | Dev and failed testing | 6 Boards | Radio Button | y |  | Working |  | cfg/i/gc/boardCount/powerComm | 6
| Board 1 | Dev and failed testing | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/powerComm/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/BIN/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/BIN/3/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/hasPressure | boolean | [12 empty] | Ourside EXV2 does not publish
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/hasTemperature | boolean
| Comm 2 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/hasPressure | boolean
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/hasTemperature | boolean
| Comm 3 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/hasPressure | boolean
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/hasTemperature | boolean
| Comm 4 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/hasPressure | boolean
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/hasTemperature | boolean
| Comm 5 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 2 | Dev and failed testing | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/powerComm/2/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/BIN/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/BIN/3/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 3 | Dev and failed testing | Unique ID | Radio Button or Status |  |  | Working |  | cfg/i/gc/boards/powerComm/3/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/BIN/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/BIN/3/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 4 | Dev and failed testing | Unique ID | Radio Button or Status | n |  | Working |  | cfg/i/gc/boards/powerComm/4/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/BIN/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/BIN/3/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 5 | Dev and failed testing | Unique ID | Radio Button or Status | n |  | Working |  | cfg/i/gc/boards/powerComm/5/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/BIN/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/BIN/3/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 6 | Dev and failed testing | Unique ID | Radio Button or Status | n |  | Working |  | cfg/i/gc/boards/powerComm/6/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/BIN/2/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/BIN/3/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor | Radio Button | y |  | Working |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Child Checkbox | n |  | Working | Dev Completed | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasTemperature | true
Can't Test
Cooling Board |  | Unknown
Can't Test
Cooling Board | Count | Dev and failed testing | 1 Board |  |  |  | Working |  | cfg/i/gc/boardCount/cooling | 1
|  | Dev and failed testing | 2 Boards |  |  |  | Working |  | cfg/i/gc/boardCount/cooling | 2
|  | Dev and failed testing | 3 Boards |  |  |  | Working |  | cfg/i/gc/boardCount/cooling | 3
|  | Dev and failed testing | 4 Boards |  |  |  | Working |  | cfg/i/gc/boardCount/cooling | 4
| Board 1 | Dev and failed testing | Unique ID | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | Radio Button | n | I don't need these, so UI only if you do need them | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | none | ui/config/cooling/1/compressorSetup | none
|  | Dev and failed testing | Single Compressor | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | compressor | ui/config/cooling/1/compressorSetup | single
|  | Dev and failed testing | Tandem | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | compressor | ui/config/cooling/1/compressorSetup | tandem
| Compressor 1 Type | Dev and passed testing | Digital | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/make | none
|  | Unknown | Danfoss | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/make | danfoss
|  | Unknown | 0-10V | Child Checkbox | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None |  |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/tonnage
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/make | none
|  | Not Tested | Danfoss | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/make | danfoss
|  | Not Tested | 0-10V | Child Checkbox | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None |  |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and failed testing | Tonnage | Setpoint |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/tonnage
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  | Working |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/A2L/1/selection | none
|  | Not Tested | Cabinet | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/A2L/1/selection | cabinet
|  | Not Tested | Air Stream | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/A2L/1/selection | airstream
| Mout 1 | Dev and failed testing | Not used | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | none
|  | Dev and failed testing | Unloader | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | unloader
|  | Dev and failed testing | Compressor Enable (Step) | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | compressorEnable(step)
|  | Dev and failed testing | Startup Solenoid | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | startupSolenoid
|  | Dev and failed testing | Reversing Valve | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | reversingValve
|  | Dev and failed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and failed testing | Not used | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | none
|  | Dev and failed testing | Unloader | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | unloader
|  | Dev and failed testing | Compressor Enable (Step) | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | compressorEnable(step)
|  | Dev and failed testing | Startup Solenoid | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | startupSolenoid
|  | Dev and failed testing | Reversing Valve | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | reversingValve
|  | Dev and failed testing | BACnet Passthrough | Radio Button | n |  | Working |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used | Radio Button | n |  | NA
|  | Not Tested | Superheat | Radio Button | n | Unused for now | NA
|  | Not Tested | Subcooling | Radio Button | n |  | NA
| Harness 2 | Not Tested | Not used | Radio Button | n |  | NA
|  | Not Tested | Superheat | Radio Button | n |  | NA
|  | Not Tested | Subcooling | Radio Button | n |  | NA
| Analog Input 1 | Not Tested | Not Used | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  | NA |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used | Radio Button | ny |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used | Radio Button | ny |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used | Radio Button | ny |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  | NA |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable | Radio Button | n |  | Working | here, in topic the board spelling is incorrect | cfg/i/gc/boards/cooling/1/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable | Radio Button | y |  | Working | here, in topic the board spelling is incorrect | cfg/i/gc/boards/cooling/1/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps | Radio Button | n |  | Working | here, in topic the board spelling is incorrect | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | 2800 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps | Radio Button | n |  | Working | here, in topic the board spelling is incorrect | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | 3500 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps | Radio Button | n |  | Working | here, in topic the board spelling is incorrect | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | 6386 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Factry Custom | Radio Button | n |  | Working | Same topic | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | [13 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out
| Board 2 | Dev and failed testing | Unique ID | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | Radio Button | n | I don't need these, so UI only if you do need them |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | none | ui/config/cooling/2/compressorSetup | none
|  | Dev and failed testing | Single Compressor | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | compressor | ui/config/cooling/2/compressorSetup | single
|  | Dev and failed testing | Tandem | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | compressor | ui/config/cooling/2/compressorSetup | tandem
| Compressor 1 Type | Dev and passed testing | Digital | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/make | none
|  | Not Tested | Danfoss | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/make | danfoss
|  | Not Tested | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [5 empty] | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/tonnage
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/make | none
|  | Not Tested | Danfoss | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/make | danfoss
|  | Not Tested | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [5 empty] | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/tonnage
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/A2L/1/selection | none
|  | Not Tested | Cabinet | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/A2L/1/selection | cabinet
|  | Not Tested | Air Stream | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/A2L/1/selection | airstream
| Mout 1 | Dev and failed testing | Not used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | none
|  | Dev and failed testing | Unloader | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | unloader
|  | Dev and failed testing | Compressor Enable (Step) | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | compressorEnable(step)
|  | Dev and failed testing | Startup Solenoid | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | startupSolenoid
|  | Dev and failed testing | Reversing Valve | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | reversingValve
|  | Dev and failed testing | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and failed testing | Not used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | none
|  | Dev and failed testing | Unloader | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | unloader
|  | Dev and failed testing | Compressor Enable (Step) | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | compressorEnable(step)
|  | Dev and failed testing | Startup Solenoid | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | startupSolenoid
|  | Dev and failed testing | Reversing Valve | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | reversingValve
|  | Dev and failed testing | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used | Radio Button | n
|  | Not Tested | Superheat | Radio Button | n | Unused for now
|  | Not Tested | Subcooling | Radio Button | n
| Harness 2 | Not Tested | Not used | Radio Button | n
|  | Not Tested | Superheat | Radio Button | n
|  | Not Tested | Subcooling | Radio Button | n
| Analog Input 1 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/2/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable | Radio Button | y |  |  |  | cfg/i/gc/boads/cooling/2/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/2/ReheatValve/1/stepCount | 2800 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/2/ReheatValve/1/stepCount | 3500 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/2/ReheatValve/1/stepCount | 6386 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom | Radio Button | n | [17 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out
| Board 3 | Not Tested | Unique ID | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | Radio Button | n | I don't need these, so UI only if you do need them |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | none | ui/config/cooling/3/compressorSetup | none
|  | Dev and failed testing | Single Compressor | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | compressor | ui/config/cooling/3/compressorSetup | single
|  | Dev and failed testing | Tandem | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | compressor | ui/config/cooling/3/compressorSetup | tandem
| Compressor 1 Type | Dev and passed testing | Digital | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/make | none
|  | Unknown | Danfoss | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/make | danfoss
|  | Unknown | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [5 empty] | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/tonnage
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/make | none
|  | Not Tested | Danfoss | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/make | danfoss
|  | Not Tested | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [5 empty] | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/tonnage
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/A2L/1/selection | none
|  | Not Tested | Cabinet | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/A2L/1/selection | cabinet
|  | Not Tested | Air Stream | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/A2L/1/selection | airstream
| Mout 1 | Dev Partial Testing | Not used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | none
|  | Dev Partial Testing | Unloader | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | unloader
|  | Dev Partial Testing | Compressor Enable (Step) | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | compressorEnable(step)
|  | Dev Partial Testing | Startup Solenoid | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | startupSolenoid
|  | Dev Partial Testing | Reversing Valve | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | reversingValve
|  | Dev Partial Testing | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev Partial Testing | Not used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | none
|  | Dev Partial Testing | Unloader | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | unloader
|  | Dev Partial Testing | Compressor Enable (Step) | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | compressorEnable(step)
|  | Dev Partial Testing | Startup Solenoid | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | startupSolenoid
|  | Dev Partial Testing | Reversing Valve | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | reversingValve
|  | Dev Partial Testing | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used | Radio Button | n
|  | Not Tested | Superheat | Radio Button | n | Unused for now
|  | Not Tested | Subcooling | Radio Button | n
| Harness 2 | Not Tested | Not used | Radio Button | n
|  | Not Tested | Superheat | Radio Button | n
|  | Not Tested | Subcooling | Radio Button | n
| Analog Input 1 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/3/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable | Radio Button | y |  |  |  | cfg/i/gc/boads/cooling/3/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/3/ReheatValve/1/stepCount | 2800 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/3/ReheatValve/1/stepCount | 3500 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/3/ReheatValve/1/stepCount | 6386 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom | Radio Button | n | [17 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out
| Board 4 | Dev and failed testing | Unique ID | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | Radio Button | n | I don't need these, so UI only if you do need them |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | none | ui/config/cooling/4/compressorSetup | none
|  | Dev and failed testing | Single Compressor | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | compressor | ui/config/cooling/4/compressorSetup | single
|  | Dev and failed testing | Tandem | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | compressor | ui/config/cooling/4/compressorSetup | tandem
| Compressor 1 Type | Dev and passed testing | Digital | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/make | none
|  | Unknown | Danfoss | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/make | danfoss
|  | Unknown | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [5 empty] | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/tonnage
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/make | none
|  | Unknown | Danfoss | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/make | danfoss
|  | Unknown | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [5 empty] | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | none | [12 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | none
|  | Not Developed | YAW0471E-5X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0471E-2X9-ASH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and passed testing | Tonnage | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/tonnage
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/A2L/1/selection | none
|  | Not Tested | Cabinet | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/A2L/1/selection | cabinet
|  | Not Tested | Air Stream | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/A2L/1/selection | airstream
| Mout 1 | Dev and failed testing | Not used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | none
|  | Dev and failed testing | Unloader | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | unloader
|  | Dev and failed testing | Compressor Enable (Step) | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | compressorEnable(step)
|  | Dev and failed testing | Startup Solenoid | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | startupSolenoid
|  | Dev and failed testing | Reversing Valve | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | reversingValve
|  | Dev and failed testing | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and failed testing | Not used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | none
|  | Dev and failed testing | Unloader | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | unloader
|  | Dev and failed testing | Compressor Enable (Step) | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | compressorEnable(step)
|  | Dev and failed testing | Startup Solenoid | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | startupSolenoid
|  | Dev and failed testing | Reversing Valve | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | reversingValve
|  | Dev and failed testing | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used | Radio Button | n
|  | Not Tested | Superheat | Radio Button | n | Unused for now
|  | Not Tested | Subcooling | Radio Button | n
| Harness 2 | Not Tested | Not used | Radio Button | n
|  | Not Tested | Superheat | Radio Button | n
|  | Not Tested | Subcooling | Radio Button | n
| Analog Input 1 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection
|  | Not Tested | Defrost Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection
|  | Not Tested | Defrost Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | none
|  | Not Tested | Supply Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/4/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable | Radio Button | y |  |  |  | cfg/i/gc/boads/cooling/4/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/4/ReheatValve/1/stepCount | 2800 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/4/ReheatValve/1/stepCount | 3500 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps | Radio Button | n |  |  |  | cfg/i/gc/boads/cooling/4/ReheatValve/1/stepCount | 6386 | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom | Radio Button | n | [17 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out

## Air Handler Board
Section | Page | State | Feature | Type | Chevron? | Topic Notes | QA Status | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Air Handler Board | Count | Dev and passed testing | 1 Board | Radio Button | n |  | Working | cfg/i/gc/boardCount/airHandler | 1
|  | Dev and passed testing | 2 Boards | Radio Button | n |  | Working | cfg/i/gc/boardCount/airHandler | 2
| Air Handler Board 1 | Dev and failed testing | Unique ID | Radio Button or Status |  |  | Working | cfg/i/gc/boards/airHandler/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
A2L Port | A2L Port 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/1/selection | none
|  | Dev and passed testing | Cabinet | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/1/selection | cabinet
|  | Dev and passed testing | Airstream | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/1/selection | airstream
| A2L Port 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/2/selection | none
|  | Dev and passed testing | Cabinet | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/2/selection | cabinet
|  | Dev and passed testing | Airstream | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/2/selection | airstream
| A2L Port 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/3/selection | none
|  | Dev and passed testing | Cabinet | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/3/selection | cabinet
|  | Dev and passed testing | Airstream | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/A2L/3/selection | airstream
VFD Ports | VFD Port 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  | This data is tied to the VFD port, make sure the PinLocation is in the topic correctly for all motor data entries | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/1/isLeadFan | false
| VFD Port 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/2/isLeadFan | false
| VFD Port 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/3/isLeadFan | false
| VFD Port 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/4/isLeadFan | false
| VFD Port 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/5/isLeadFan | false
| VFD Port 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/VFD/6/isLeadFan | false
Enable | X Fan Enable | Not Tested | None | Radio Button | n |  | On hold | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | none
|  | Not Tested | AHU Board X, Analog Output Y | Radio Button | n |  | On hold | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | airHandler/#/MOUT/*
Damper Port | Damper Port | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | none
|  | Dev and passed testing | Return Air | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | raDamper
|  | Dev and passed testing | Return Air Bypass | Radio Button |  |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | rabDamper
|  | Dev and passed testing | Exhaust Air | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | motorizedExhaustDamper
| Return Air End Switch | Dev and passed testing | Disabled | Radio Button | n | These are connected to what is selected for this damper port, topics are the same | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | true
| Exhaust Air End Switch | Dev and passed testing | Disabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | true
Analog Inputs | Duct Static Pressure | Dev and passed testing | Disabled | Radio Button | n | Why isn't this labeled as an AIN or 0-10V? Need to double check this one that it is actually supposed to be AIN1 | Working | cfg/i/gc/boards/airHandler/1/STATIC/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/STATIC/1/selection | ductStaticPressure
| Thermistor 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/1/selection | none
|  | Dev and passed testing | Supply Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/1/selection | saTemp
|  | Dev and passed testing | Space Temperature | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/1/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/1/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/1/selection | raTemp
|  | Not Developed | Service Factor | Radio Button | n |  | NA | cfg/i/gc/boards/airHandler/1/THERM/1/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/1/selection | BACnetPassthrough
| Thermistor 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/2/selection | none
|  | Dev and passed testing | Supply Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/2/selection | saTemp
|  | Dev and passed testing | Space Temperature | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/2/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/2/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/2/selection | raTemp
|  | Not Developed | Service Factor | Radio Button | n |  | NA | cfg/i/gc/boards/airHandler/1/THERM/2/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/THERM/2/selection | BACnetPassthrough
| 0-10V | Dev and passed testing | Not Used | Radio Button | n | See note above about Duct Static Pressure, is this AIN1? AIN2? | Working | cfg/i/gc/boards/airHandler/1/AIN/1/selection | none
|  | Dev and passed testing | Exhaust Duct Static Pressure | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AIN/1/selection | exhaustDuctStaticPressure
|  | Dev and passed testing | Building Pressure | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AIN/1/selection | buildingPressure
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AIN/1/selection | BACnetPassthrough
Analog Outputs | Analog Output 1 | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | none
|  | Dev and passed testing | Modulating Chilled Water | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | BACnetPassthrough
| Analog Output 2 | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | none
|  | Dev and passed testing | Modulating Chilled Water | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | BACnetPassthrough
Mouts | Mout 1 NOTE: Override Active is missin | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | BACnetPassthrough
Enable | X Fan Enable | Dev and failed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | none
|  | Dev and failed testing | AHU Board X, Analog Output Y | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | airHandler/#/MOUT/*
Binary Inputs | Binary Input 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | remoteOccupied
|  | Dev and failed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/2/selection | BACnetPassthrough
| Binary Input 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/3/selection | BACnetPassthrough
| Binary Input 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/4/selection | BACnetPassthrough
| Binary Input 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/5/selection | BACnetPassthrough
| Binary Input 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/6/selection | BACnetPassthrough
| Binary Input 7 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/7/selection | BACnetPassthrough
| Binary Input 8 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/1/BIN/8/selection | BACnetPassthrough
Board 2 | Air Handler Board 2 | Dev and failed testing | Unique ID | Radio Button or Status |  |  | Working | cfg/i/gc/boards/airHandler/2/uuid |  | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
A2L Port | A2L Port 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/1/selection | none
|  | Dev and passed testing | Cabinet | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/1/selection | cabinet
|  | Dev and passed testing | Airstream | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/1/selection | airstream
| A2L Port 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/2/selection | none
|  | Dev and passed testing | Cabinet | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/2/selection | cabinet
|  | Dev and passed testing | Airstream | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/2/selection | airstream
| A2L Port 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/3/selection | none
|  | Dev and passed testing | Cabinet | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/3/selection | cabinet
|  | Dev and passed testing | Airstream | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/A2L/3/selection | airstream
VFD Ports | VFD Port 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/1/isLeadFan | false
| VFD Port 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/2/isLeadFan | false
| VFD Port 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/3/isLeadFan | false
| VFD Port 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/4/isLeadFan | false
| VFD Port 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/5/isLeadFan | false
| VFD Port 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/selection | none
|  | Dev and passed testing | Supply Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/selection | supplyFan
|  | Dev and passed testing | Return Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/selection | returnFan
|  | Dev and passed testing | Exhaust Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/selection | condenserFan
|  | Dev and passed testing | Heat Wheel | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/overloadInput | none
|  | Dev and passed testing | Overload Input 1 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/vfdPortType | none
|  | Dev and passed testing | Communicating | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/vfdPortType | commFan
|  | Dev and passed testing | 0-10 | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/RPM
|  | Dev and passed testing | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/RPM
|  | Not Developed | Service Factor | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/nameplateFreq
|  | Dev and passed testing | Ld | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.Ld
|  | Dev and passed testing | Lq | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.Lq
|  | Dev and passed testing | BEMF | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.BEMF
|  | Dev and passed testing | Rs | Setpoint |  |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.Rs
| Voltage | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/isLeadFan | true
|  | Dev and passed testing | Lag | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/VFD/6/isLeadFan | false
Damper Port | Damper Port | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | none
|  | Dev and passed testing | Return Air | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | raDamper
|  | Dev and passed testing | Return Air Bypass | Radio Button |  |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | rabDamper
|  | Dev and passed testing | Exhaust Air | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | motorizedExhaustDamper
| Return Air End Switch | Dev and passed testing | Disabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | true
| Exhaust Air End Switch | Dev and passed testing | Disabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | true
Analog Inputs | Duct Static Pressure | Dev and passed testing | Disabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/STATIC/1/selection | none
|  | Dev and passed testing | Enabled | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/STATIC/1/selection | ductStaticPressure
| Thermistor 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | none
|  | Dev and passed testing | Supply Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | saTemp
|  | Dev and passed testing | Space Temperature | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | raTemp
|  | Not Developed | Mixed Air Temperature | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/1/selection | BACnetPassthrough
| Thermistor 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | none
|  | Dev and passed testing | Supply Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | saTemp
|  | Dev and passed testing | Space Temperature | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | raTemp
|  | Not Developed | Mixed Air Temperature | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/THERM/2/selection | BACnetPassthrough
| 0-10V | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AIN/1/selection | none
|  | Dev and passed testing | Exhaust Duct Static Pressure | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AIN/1/selection | exhaustDuctStaticPressure
|  | Dev and passed testing | Building Pressure | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AIN/1/selection | buildingPressure
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AIN/1/selection | BACnetPassthrough
Analog Outputs | Analog Output 1 | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | none
|  | Dev and passed testing | Modulating Chilled Water | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | BACnetPassthrough
| Analog Output 2 | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | none
|  | Dev and passed testing | Modulating Chilled Water | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | BACnetPassthrough
Mouts | Mout 1 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Dev and passed testing | Not Used | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | none
|  | Dev and passed testing | Reversing Valve | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | reversingValve
|  | Dev and passed testing | ERV | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable | Radio Button | y |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active | Radio Button | n |  | Working | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | econoActive
|  | Dev and passed testing | Occupied Active | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | occupiedActive
|  | Dev and failed testing | Override Active | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | overrideActive
|  | Dev and passed testing | Alarm Active | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | alarmActive
|  | Dev and passed testing | Reheat Active | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | reheatActive
|  | Dev and passed testing | Heat Enable | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Cool Enable | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | coolEnable
|  | Dev and passed testing | Preheat Enable | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | BACnetPassthrough
Binary Inputs | Binary Input 1 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | BACnetPassthrough
| Binary Input 3 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | BACnetPassthrough
| Binary Input 4 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | BACnetPassthrough
| Binary Input 5 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | BACnetPassthrough
| Binary Input 6 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | BACnetPassthrough
| Binary Input 7 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | BACnetPassthrough
| Binary Input 8 | Dev and passed testing | Not Used | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | none
|  | Dev and passed testing | Hood On | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough | Radio Button | n |  |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | BACnetPassthrough

## Sensors
Section | Page | Status | Feature | Type | Chevron? | Topic Notes | QA Status | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Space Sensor | Type | Dev and passed testing | No Space Sensor | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/spaceSensorType | none
|  | Dev and passed testing | Analog | Radio Button | y |  | Working | cfg/i/gc/sensorConfig/spaceSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | y |  | Working | cfg/i/gc/sensorConfig/spaceSensorType | digital
|  | Dev and passed testing | TS Space Sensor | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/spaceSensorType | tsSpace
|  | Dev and passed testing | BACnet Temp | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/spaceSensorType | bacnet
|  | Dev and failed testing | Plus Humidity | Child Checkbox | n | Treat this like another Radio Button in the list | Working | cfg/i/gc/sensorConfig/spaceSensorType | bacnetHum
|  | Dev and failed testing | Remote Display | Checkbox | n |  | Working | cfg/i/gc/sensorConfig/spaceSensorRemoteDisplay | boolean | True when selected, False when not selected
| Analog Space Sensor SP's | Dev and passed testing | # of Space Sensors | Setpoint |  |  | Working | cfg/i/gc/sensorConfig/numSpaceSensors | integer | [6 empty] | N/A
|  | Dev and passed testing | Override | Setpoint |  |  | Working | cfg/i/manager/spaceOverride/duration | integer | [6 empty] | Hours
|  | Dev and passed testing | Setpoint Adjustment Limit | Setpoint |  |  | Working | cfg/i/manager/spaceOverride/setpointAdjust/Limit | integer | [6 empty] | F or C
| Digital Space Sensor SP's | Dev and passed testing | # of Space Sensors | Setpoint |  |  | Working | cfg/i/gc/sensorConfig/numSpaceSensors | integer | [6 empty] | N/A
|  | Dev and passed testing | Override | Setpoint |  |  | Working | cfg/i/manager/spaceOverride/duration | integer | [6 empty] | Hours
|  | Dev and passed testing | Setpoint Adjustment Limit | Setpoint |  |  | Working | cfg/i/manager/spaceOverride/setpointAdjust/Limit | integer | [6 empty] | F or C
Return Sensor | Type | Dev and passed testing | No Return Sensor | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/returnSensorType | none
|  | Dev and passed testing | Analog | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/returnSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/returnSensorType | digital
|  | Dev and passed testing | BACnet Temp | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/returnSensorType | bacnet
|  | Dev and failed testing | Plus Humidity | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/returnSensorType | bacnetHum
Outdoor Air Sensor | Type | Dev and passed testing | No OA Sensor | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/oaSensorType | none
|  | Dev and passed testing | Analog | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/oaSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/oaSensorType | digital
|  | Dev and passed testing | BACnet Temperature | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/oaSensorType | bacnet
|  | Dev and failed testing | Plus Humidity | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/oaSensorType | bacnetHum
|  | Dev and passed testing | Global Broadcast | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/oaSensorType | globalBroadcast
Supply Air Sensor | Type | Dev and passed testing | Analog | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/supplyAirSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/supplyAirSensorType | digital
CO2 Sensor | Type | Dev and passed testing | None | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/co2SensorType | none
|  | Dev and passed testing | Digital | Radio Button | y |  | Working | cfg/i/gc/sensorConfig/co2SensorType | digital
|  | Not Tested | Reads CO2 Broadcast | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/co2SensorType | co2Broadcast
|  | Not Tested | Reads CO2 from BACnet | Radio Button | n |  | Working | cfg/i/gc/sensorConfig/co2SensorType | bacnet
| CO2 Setpoints | Not Tested | CO2 Sensor Offset | Setpoint |  |  | Working | cfg/i/gc/sensorConfig/co2SensorOffset | float | [6 empty] | PPM
|  | Not Tested | CO2 Setpoint | Setpoint |  |  | Working | sp/i/iaq | float | [6 empty] | PPM
Calibration | Space Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/space/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/space/humidity
| Return Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/ra/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/ra/humidity
| Outside Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/oa/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/oa/humidity
| Supply Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/sa/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/sa/humidity
| CO2 Sensor | Not Developed | CO2 Calibration Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/space/co2

## Building Pressure
Section | Page | Status | Feature | Type | Chevron? | QA Status | QA Comments | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Type | Building Pressure Type | Dev and passed testing | Building Pressure Sensor | Radio Button | y | Working |  | test/topic/bp_sensor | buildingPressureSensor
|  | Dev and passed testing | Duct Static Pressure | Radio Button | y | Working |  | test/topic/duct_sp_sensor | buildingPressureDuctStaticPressureSensor
|  | Dev and passed testing | Fan Tracking | Radio Button | y | Working |  | cfg/i/reliefMode | ReturnFollowSupply
Building Pressure | Building Pressure Control | Not Tested | Supply Fan | Radio Button | y | Working |  | cfg/i/reliefMode | SupplyFanBuildingPressure |  |  |  |  | Must Configure Supply Fan
|  | Not Tested | Return Fan | Radio Button | y | Working |  | cfg/i/reliefMode | ReturnFanBuildingPressure |  |  |  |  | Must Configure Return Fan
|  | Not Tested | Plus Exhaust Damper | Child Checkbox | y | Working |  | cfg/i/returnFanBuildingPressure/exhaustDamper/enable | true/false |  |  |  |  | Must Configure Return Fan
|  | Not Tested | Exhaust Fan | Radio Button | y | Working |  | cfg/i/reliefMode | ExhaustFanBuildingPressure |  |  |  |  | Must Configure Exhaust Fan
|  | Not Tested | Outside Air Damper | Radio Button | y | Working |  | cfg/i/reliefMode | OADBuildingPressure |  |  |  |  | Must Configure OA Damper
|  | Dev and passed testing | Exhaust Damper | Radio Button | y | Working |  | cfg/i/reliefMode | ExhaustDamperBuildingPressure
| SF Building Pressure Setpoints | Not Tested | Building Pressure Setpoint | Setpoint |  | Working |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Not Tested | Building Pressure Deadband | Setpoint |  | Working |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Building Pressure - Return Fan Control | Can't Test | On/Off | Radio Button | n | Working |  | test/topic/on_off | buildingPressureSensorControlReturnFanControlOnOff
|  | Can't Test | Modulating | Radio Button | n | Working |  | test/topic/modulating | buildingPressureSensorControlReturnFanControlModulating
| RF Building Pressure Setpoints | Not Tested | Building Pressure Setpoint | Setpoint |  | Working |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Not Tested | Building Pressure Deadband | Setpoint |  | Working |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Plus Exhaust Damper Setpoints | Not Tested | Exhaust Damper Setpoint | Setpoint |  | Working |  | sp/i/exhaust/damper/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 0.2 | 0.1
|  | Not Tested | Exhaust Damper Deadband | Setpoint |  | Working |  | sp/i/exhaust/damper/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01
| Building Pressure - Exhaust Fan Control | Can't Test | On/Off | Radio Button | n | Working |  | test/topic/on_off | buildingPressureSensorControlReturnFanControlOnOff
|  | Can't Test | Modulating | Radio Button | n | Working |  | test/topic/modulating | buildingPressureSensorControlReturnFanControlModulating
| EF Building Pressure Setpoints | Not Tested | Building Pressure Setpoint | Setpoint |  | Working |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Not Tested | Building Pressure Deadband | Setpoint |  | Working |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| OA Damper Building Pressure Setpoints | Not Tested | Building Pressure Setpoint | Setpoint |  | Working |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Not Tested | Building Pressure Deadband | Setpoint |  | Working |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Exhaust Damper Building Pressure Setpoints | Not Tested | Building Pressure Setpoint | Setpoint |  | Working |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Not Tested | Building Pressure Deadband | Setpoint |  | Working |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Building Pressure Sensor Type | Dev and passed testing | None | Radio Button | n | Working |  | cfg/i/gc/sensorConfig/buildingPressureSensorType | none
|  | Dev and failed testing | Analog | Radio Button | n | Working |  | cfg/i/gc/sensorConfig/buildingPressureSensorType | analog
|  | Can't Test | Exhaust Fan | Radio Button | n | Working |  | test/topic//bp/ef | buildingPressureSensorTypeExhaustFan
|  | Can't Test | Outside Air Damper | Radio Button | n | Working |  | test/topic//bp/oad | buildingPressureSensorTypeOutsideAirDamper
Duct Static Pressure Sensor | Duct Static Type | Not Tested | Return Fan | Checkbox | y | Working |  | cfg/i/ductStaticControl/return/enabled | true/false
|  | Not Tested | Exhaust Fan | Checkbox | y | Working |  | cfg/i/ductStaticControl/exhaust/enabled | true/false
| RF Duct Static Setpoints | Not Tested | Duct Static Pressure Setpoint | Setpoint |  | Working |  | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the return/exhaust fan. The return/exhaust fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Not Tested | Duct Static Pressure Deadband | Setpoint |  | Working |  | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.01 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
| EF Duct Static Setpoints | Dev and failed testing | Duct Static Pressure Setpoint | Setpoint |  | Working |  | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the return/exhaust fan. The return/exhaust fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and failed testing | Duct Static Pressure Deadband | Setpoint |  | Working |  | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.01 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
Fan Tracking | Type | Dev and passed testing | Return Fan | Checkbox | y | Working |  | cfg/i/returnFollowSupply/return/enabled | true/false
|  | Dev and passed testing | Exhaust Fan | Checkbox | y | Working |  | cfg/i/returnFollowSupply/exhaust/enabled | true/false
| Return Fan Tracking | Dev and passed testing | Tracking Percent | Setpoint |  | Working |  | cfg/i/returnFollowSupply/scaling | [7 empty] | % | 0 | 125 | 100 | The return fan will track the supply fan at this percentage.
|  | Dev and passed testing | Return Fan Minimum Fan Speed | Setpoint |  | Working |  | cfg/i/returnFollowSupply/min | [7 empty] | % | 0 | 100 | 0 | The return fan is allowed to modulate down to this speed
|  | Dev and failed testing | Tracking Percent | Setpoint |  | Working |  | cfg/i/exhaustFollowSupply/scaling | [7 empty] | % | 0 | 125 | 100 | The exhaust fan will track the supply fan at this percentage.
|  | Dev and failed testing | Exhaust Fan Minimum Fan Speed | Setpoint |  | Working |  | cfg/i/exhaustFollowSupply/min | [7 empty] | % | 0 | 100 | 0 | The exhaust fan is allowed to modulate down to this speed.

## OA Damper
Section | Page | State | Feature | Type | Chevron? | QA Status | QA Comments | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Config | OA Config | Dev and passed testing | No Economizer Control | Radio Button | n | Working |  | cfg/i/manager/economizerControl | none
|  | Dev and passed testing | Standard Economizer Control | Radio Button | n | Working |  | cfg/i/manager/economizerControl | standard
|  | Dev and passed testing | Economizer Control with IAQ Override | Radio Button | y | Working |  | cfg/i/manager/economizerControl | iaq
|  | Dev and passed testing | Building Pressure Control | Radio Button | y | Working |  | cfg/i/pressureRelief | OADBuildingPressure |  |  | cfg/i/pressureRelief
|  | Dev and failed testing | Allow Economizer During Unoccupied Mode | Radio Button | n | Working |  | cfg/i/manager/unoccEconoEnable | boolean
|  | Dev and failed testing | Fault Detection Diagnostics | Radio Button | n | Working |  | cfg/i/economizer/faultDetectionDiagnostics | boolean
Min Pos | Min Pos | Dev and passed testing | Minimum Economizer Position | Setpoint |  | Working |  | cfg/oa/damper/minPosition | integer | [6 empty] | % | 0 | 100 | 10 | Enter the desired minimum outdoor air damper position for fresh air requirements during occupied times. The Economizer damper will be allowed to modulate up from this minimum position to 100% outdoor air as needed for cooling or CO2 demand control ventilation but will not go below. The economizer must be configured and the unit must be in Occupied Mode for all HVAC applications.
Enable | OA Damper Enable | Dev and passed testing | Outside Air Drybulb | Radio Button | y | Working |  | cfg/economizeEnableMethod | OADrybulb
|  | Dev and passed testing | Outside Air Wetbulb | Radio Button | y | Working |  | cfg/economizeEnableMethod | OAWetbulb
|  | Dev and passed testing | Outside Air Dewpoint | Radio Button | y | Working |  | cfg/economizeEnableMethod | OADewpoint
|  | Not Tested | Comparative w/ Drybulb Limit | Radio Button | y | InCorrect |  | cfg/economizeEnableMethod | ComparativeEnthalpyDryBulb
|  | Not Tested | Comparative Enthalpy | Radio Button | y | InCorrect |  | cfg/economizeEnableMethod | ComparativeEnthalpy
| OA Drybulb | Not Tested | OA Enable Setpoint | Setpoint |  |  | Duplicate topic | cfg/economizeSetpoint | integer | [6 empty] | F or C | -30 | 80 | 55 | This is the setpoint in which the unit will enter the economizer mode based on the enable selection i.e. dry bulb, wet bulb, dewpoint, comparative enthalpy, or comparative w/ dry bulb limit.
| OA Wetbulb | Not Tested | OA Enable Setpoint | Setpoint |  |  | Duplicate topic | cfg/economizeSetpoint | integer | [6 empty] | F or C | -30 | 80 | 55 | This is the setpoint in which the unit will enter the economizer mode based on the enable selection i.e. dry bulb, wet bulb, dewpoint, comparative enthalpy, or comparative w/ dry bulb limit.
| OA Dewpoint | Not Tested | OA Enable Setpoint | Setpoint |  |  | Duplicate topic | cfg/economizeSetpoint | integer | [6 empty] | F or C | -30 | 80 | 55 | This is the setpoint in which the unit will enter the economizer mode based on the enable selection i.e. dry bulb, wet bulb, dewpoint, comparative enthalpy, or comparative w/ dry bulb limit.
| Comparative Enthalpy w/ Drybulb Limit | Not Tested | OA Limit Setpoint | Setpoint |  |  | Duplicate topic | cfg/economizeSetpoint | integer | [6 empty] | F or C
|  | Not Tested | OA Enthalpy Setpoint | Setpoint |  | Working |  | cfg/economizeEnthalpySetpoint | integer | [6 empty] | BTU/lb | 12 | 35 | 28 | This the Enthalpy Enable Setpoint for Comparative Enthalpy Economizer Operation.
|  | Not Tested | Enthalpy Deadband | Setpoint |  | Working |  | cfg/economizeEnthalpyDeadband | float | [6 empty] | BTU/lb | 0.3 | 15 | 0.5 | This the Enthalpy Enable Deadband for Comparative Enthalpy Economizer Operation.
| Comparative Enthalpy w/ Drybulb Limit | Not Tested | OA Enthalpy | Setpoint |  |  | Duplicate topic | cfg/economizeEnthalpySetpoint | integer | [6 empty] | BTU/lb
|  | Not Tested | Enthalpy Deadband | Setpoint |  |  | Duplicate topic | cfg/economizeEnthalpyDeadband | float | [6 empty] | BTU/lb
Voltages | Voltages | Not Tested | Minimum Economizer Voltage | Setpoint |  | Working |  | cfg/i/economizer/voltage/min | integer | [6 empty] | VDC | 0 | 10 | 10 | Enter the maximum voltage for economizer full open position.
|  | Not Tested | Maximum Economizer Voltage | Setpoint |  | Working |  | cfg/i/economizer/voltage/max | integer | [6 empty] | VDC | 0 | 10 | 0 | Enter the minimum voltage for economizer full closed position.

## Dehum
Section | Page | Status | Feature | Type | Chevron? | Topic Notes | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Config | Config | Dev and failed testing | No Dehum | Radio Button | n | Working | cfg/i/dehum/enabled | false
|  | Dev and failed testing | Humidity Control | Radio Button | y | Working | cfg/i/dehum/usesDewpoint | false | cfg/i/dehum/enabled | true
|  | Dev and failed testing | Dewpoint Control | Radio Button | y | Working | cfg/i/dehum/usesDewpoint | true | cfg/i/dehum/enabled | true
|  | Dev and failed testing | Enable Dehum in All Unit Operations | Radio Button | n | Working | cfg/i/dehum/isPriority | true | cfg/i/dehum/enabled | true
|  | Can't Test | Vent (standard mode only) | Checkbox | y | Working | test/topic/dehum_vent | dehumEnableVent:true
|  | Can't Test | Cool | Child Checkbox | n | Working | test/topic/dehum_cool | dehumEnableCool:true
|  | Can't Test | Heat | Child Checkbox | n | Working | test/topic/dehum_heat | dehumEnableHeat:true
|  | Not Tested | Unoccupied | Child Checkbox | n | Working | cfg/i/dehum/whileUnoccupied | true
| Enable Sensor | Dev and failed testing | No Enable Sensor | Radio Button | n | Working | cfg/i/dehum/enableSensor | none
|  | Dev and passed testing | Space Sensor | Radio Button | y | Working | cfg/i/dehum/enableSensor | Space |  |  |  |  | Must Configure Space Sensor
|  | Dev and passed testing | Return Sensor | Radio Button | y | Working | cfg/i/dehum/enableSensor | Return |  |  |  |  | Must Configure Return Sensor
|  | Dev and passed testing | OA Sensor | Radio Button | y | Working | cfg/i/dehum/enableSensor | OA |  |  |  |  | Must Configure OA Sensor
|  | Dev and failed testing | Supply Air Dewpoint Control (Sensor Must Use Digital Temp/Hum) | Child Checkbox | y | Working | cfg/i/dehum/supplyAirDewpointControl/enable | true/false |  |  |  |  | Sensor must use Digital Temp/Hum
| Humidity Setpoints | Not Tested | Humidity Setpoint | Setpoint |  | Working | sp/i/rhCoolSPLo | integer | [6 empty] | % | 0 | 100 | 50
|  | Not Tested | Humidity OAT Lockout | Setpoint |  | Working | cfg/i/dehum/oatLockout | integer | [6 empty] | F or C | -30 | 110 | 60
| Dewpoint Setpoints | Can't Test | Dewpoint Setpoint | Setpoint |  | Working | cfg/i/dehum/supplyAirDewpointControl/enable | true/false | [6 empty] | F or C | 0 | 110 | 50
|  | Not Tested | Dewpoint OAT Lockout | Setpoint |  | Working | cfg/i/dehum/oatLockout | integer | [6 empty] | F or C | -30 | 110 | 60
| Supply Air Dewpoint Setpoint | Can't Test | Supply Air Dewpoint Setpoint | Setpoint | [10 empty] | F or C
Reheat | Reheat Config | Dev and failed testing | No Reheat | Radio Button | n | Unnecessary, if there's a reheat valve assigned to the circuit, we have Modulating HGR reheat by default. Really we just need a choice between none, aux, and unit Heat. Likewise, if a Return Bypass is configured, we will use that | cfg/i/refrig/reheat/additionalSource | none
|  | Can't Test | Modulating HGR | Radio Button | y
|  | Not Tested | No Additional Reheat | Child Radio | n |  | cfg/i/refrig/reheat/additionalSource | none
|  | Not Tested | Plus Aux Heat (Heat Pump Required) | Child Radio | n |  | cfg/i/refrig/reheat/additionalSource | Aux |  |  |  |  | Must Configure Heat Pump
|  | Not Tested | Plus Unit Heat (call factory) | Child Radio | y |  | cfg/i/refrig/reheat/additionalSource | UnitHeat |  |  |  |  | Call Factory
|  | Dev and failed testing | Unit Heat for Reheat | Radio Button | n |  | cfg/i/refrig/reheat/additionalSource | UnitHeat
|  | Can't Test | On/Off | Radio Button | n |  | cfg/i/gc/fanConfig/heatWheel/controlMethod | onOff
|  | Can't Test | Plus Unit Heat | Child Checkbox | y |  | cfg/i/refrig/reheat/additionalSource | plusUh:true
|  | Can't Test | Has Return Bypass Control | Checkbox | n |  | test/topic/dehum_reheat_has_return | returnBypassControl
|  | Can't Test | SAT Control | Child Checkbox | n |  | test/topic/dehum_reheat_sat_control | satControl:true
| Flush | Dev and failed testing | Enable Startup Flush | Checkbox | n | Working | cfg/i/reheatFlush/enableStartupFlush | true
|  | Dev and failed testing | Enable Reheat Flush | Checkbox | y | Working | cfg/i/reheatFlush/enableReheatFlush | true
|  | Dev and failed testing | Enable Condenser Flush | Checkbox | y | Working | cfg/i/reheatFlush/enableOutdoorFlush | true
|  | Dev and failed testing | Enable Cooling Flush | Checkbox | y | Working | cfg/i/reheatFlush/enableCoolingFlush | true
| Reheat Flush Int | Not Tested | Reheat Flush Interval | Setpoint |  | Working | cfg/i/reheatFlush/reheatIntervalTime
| Cond Flush Int | Not Tested | Condenser Flush Interval | Setpoint |  | Working | cfg/i/reheatFlush/condenserIntervalTime
| Cool Flush Int | Not Tested | Cooling Flush Interval | Setpoint |  | Working | cfg/i/reheatFlush/coolIntervalTime
| Valves | Not Tested | 2800 Steps | Radio Button | n |  | pcfg/i/systemConfig/_/unitConfig/refrigerationSystem/circuits/A/Reheat/interface/stepCount
|  | Not Tested | 3500 Steps | Radio Button | n |  | pcfg/i/systemConfig/_/unitConfig/refrigerationSystem/circuits/A/Reheat/interface/stepCount
|  | Not Tested | 6386 Steps | Radio Button | n |  | pcfg/i/systemConfig/_/unitConfig/refrigerationSystem/circuits/A/Reheat/interface/stepCount
|  | Not Tested | Facotry Custom | Radio Button | n | [15 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot

## Filters
Section | Page | Status | Feature | Type | Chevron? | QA Comments | Dev Comment | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Filters | Type | Can't Test | Pre | Checkbox | y | Working |  | test/topic/pre_filter_monitoring | filterPre:true
|  | Can't Test | Main | Checkbox | y | Working |  | test/topic/main_filter_monitoring | filterMain:false
|  | Can't Test | Return Air Bypass | Checkbox | y | Working |  | test/topic/return_air_bypass_filter | filterReturnAirbypass:true
|  | Can't Test | Heat Wheel OA | Checkbox | y | Working |  | test/topic/heat_wheel_oa | filterHeatWheel:true |  |  |  |  | Must Configure Heat Wheel Board
|  | Can't Test | Heat Wheel Exhaust | Checkbox | y | Working |  | test/topic/heat_wheel_exhaust | filterHeatWheelExhaust:true |  |  |  |  | Must Configure Heat Wheel Board
|  | Can't Test | Preheat | Checkbox | y | Working |  | test/topic/preheat | filterPreHeat:true |  |  |  |  | Must Configure Preheat
Pre | Pre Monitoring Type | Can't Test | Binary | Radio Button | n | Working |  | test/topic/pre_binary | filterPreBinary
|  | Can't Test | Differential Pressure | Radio Button | y | Working |  | test/topic/pre_diff_pres | filterPreDifferentialPressure
|  | Can't Test | Change Interval | Radio Button | y | Working |  | test/topic/pre_cg_interval | filterPreChangeInterval
| Pre Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | test/topic/filter_pre_remaining_lifetime_differential_pressure | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint |  | Working |  | test/topic/pre_dp_setpoint | [7 empty] | " WG
|  | Can't Test | Filter Replaced | Button |  |  |  | test/topic/filter_pre_replaced
| Pre Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | test/topic/filter_pre_change_interval_remaining_lifetime | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint |  | Working |  | test/topic/pre_lifespan | [7 empty] | days
|  | Can't Test | Filter Replaced | Button |  |  |  | test/topic/filter_pre_change_interval_replaced
Main | Main Monitoring Type | Can't Test | Binary | Radio Button | n | Working |  | test/topic/main_binary | filterMainBinary
|  | Can't Test | Differential Pressure | Radio Button | y | Working |  | test/topic/main_diff_pres | filterMainDifferentialPressure
|  | Can't Test | Change Interval | Radio Button | y | Working |  | test/topic/main_cg_interval | filterMainChangeInterval
| Main Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | test/topic/filter_type_diff_main_life_time | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint |  | Working |  | test/topic/main_dp_setpoint | [7 empty] | " WG
|  | Can't Test | Filter Replaced | Button |  |  |  | test/topic/filter_type_diff_replaced
| Main Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | test/topic/filter_type_time_main_life_time | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint |  | Working |  | test/topic/main_lifespan | [7 empty] | days
|  | Can't Test | Filter Replaced | Button |  |  |  | test/topic/filter_type_time_replaced
Return Air Bypass | Return Air Bypass Monitoring Type | Can't Test | Binary | Radio Button | n | Working |  | test/topic/rab_binary | filterReturnAirByPassBinary
|  | Can't Test | Differential Pressure | Radio Button | y | Working |  | test/topic/rab_diff_pres | filterReturnAirByPassDifferentialPressure
|  | Can't Test | Change Interval | Radio Button | y | Working |  | test/topic/rab_cg_interval | filterReturnAirByPassChangeInterval
| Return Air Bypass Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  | Working | Working | sts/i/filters/ra/1/Pressure/filterLifeRemaining | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint |  | Working |  | cfg/i/filters/ra/1/pressure/airFilterDPThreshold | [7 empty] | " WG
|  | Can't Test | Filter Reset | Button |  |  |  | ctrl/i/filters/ra/1/filterReplaced
| Return Air Bypass Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | sts/i/filters/ra/1/timer/lifeTimeRemaining | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint |  | Working | Working | cfg/i/filters/ra/1/timer/filterLifespan | [7 empty] | days
|  | Can't Test | Filter Reset | Button |  |  |  | ctrl/i/filters/ra/1/filterReplaced
Heat Wheel OA | Heat Wheel OA Monitoring Type | Can't Test | Binary | Radio Button | n | Working |  | test/topic/hfo_binary | filterHeatWheelOABinary
|  | Can't Test | Differential Pressure | Radio Button | y | Working |  | test/topic/hfo_diff_pres | filterHeatWheelOADifferentialPressure
|  | Can't Test | Change Interval | Radio Button | y | Working |  | test/topic/hfo_cg_interval | filterHeatWheelOAChangeInterval
| Heat Wheel OA Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | ctrl/i/filters/heatwheel/1/diff_lifetimeremaining | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint |  | Working |  | test/topic/heat_wheel_oa_dp_setpoint | [7 empty] | " WG
|  | Can't Test | Filter Replaced | Button |  |  |  | ctrl/i/filters/heatwheel/1/diff_filterreplaced
| Heat Wheel OA Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | ctrl/i/filters/heatwheel/1/timeout_liferemaining | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint |  | Working |  | test/topic/heat_wheel_oa_lifespan | [7 empty] | days
|  | Can't Test | Filter Replaced | Button |  |  |  | ctrl/i/filters/heatwheel/1/timeout_filterreplaced
Heat Wheel Exhaust | Heat Wheel Exhaust Monitoring Type | Can't Test | Binary | Radio Button | n | Working |  | test/topic/hwe_binary | filterHeatWheelExhaustBinary
|  | Can't Test | Differential Pressure | Radio Button | y | Working |  | test/topic/hwe_diff_pres | filterHeatWheelExhaustDifferentialPressure
|  | Can't Test | Change Interval | Radio Button | y | Working |  | test/topic/hwe_cg_interval | filterHeatWheelExhaustChangeInterval
| Heat Wheel Exhaust Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | test/topic/filter_heat_wheel_exhaust_remaining_lifetime_differential_pressure | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint |  | Working |  | test/topic/heat_wheel_exhaust_dp_setpoint | [7 empty] | " WG
|  | Can't Test | Filter Replaced | Button |  |  |  | test/topic/filter_heat_wheel_exhaust_replaced
| Heat Wheel Exhaust Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  | Working | working | test/topic/filter_heat_wheel_exhaust_change_interval_remaining_lifetime | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint |  | Working | working | test/topic/heat_wheel_exhaust_lifespan | [7 empty] | days
|  | Can't Test | Filter Replaced | Button |  |  |  | test/topic/filter_remaining_lifetime_change_interval
Preheat | Preheat Monitoring Type | Can't Test | Binary | Radio Button | n | Working |  | test/topic/preh_binary | filterPreheatBinary
|  | Can't Test | Differential Pressure | Radio Button | y | Working |  | sts/i/filters/preheat/1/Pressure/filterLifeRemaining | filterPreheatDifferentialPressure
|  | Can't Test | Change Interval | Radio Button | y | Working | working | test/topic/preheat_change_interval | filterPreheatChangeInterval
| Preheat Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  | Working | working | sts/i/filters/preheat/1/pressure/filterLifeRemaining | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint |  | Working | working | cfg/i/filters/preheat/1/pressure/airFilterDPThreshold | [7 empty] | " WG
|  | Can't Test | Filter Replaced | Button |  | Working | working | ctrl/i/filters/preheat/1/filterReplaced
| Preheat Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  | Working |  | sts/i/filters/preheat/1/timer/lifeTimeRemaining | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint |  | Working |  | cfg/i/filters/preheat/1/timer/filterLifespan | [7 empty] | days
|  | Can't Test | Filter Replaced | Button |  |  |  | ctrl/i/filters/preheat/1/filterReplaced

## ERV
Section | Page | Status | Feature | Type | Chevron? | Topic Notes | QA Status | QA Comments | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Type | Type | Dev and passed testing | On/Off | Radio Button | n |  | Partially working | Off not working | cfg/i/gc/fanConfig/heatWheel/controlMethod | OnOff
|  | Dev and passed testing | Modulating | Radio Button | y |  | Working |  | cfg/i/gc/fanConfig/heatWheel/controlMethod | Modulating
| Modulating ERV | Can't Test | 0-10V | Radio Button | y | This should not be defined here, it should be defined at the board level now, as we do with all other VFDs/analogs | Working |  | test/topic/erv_type_modulating_0_to_10v | ERSTypeMod10V
|  | Can't Test | Communicating | Radio Button | n |  | Working |  | test/topic/erv_type_modulating_communicating | ERSTypeCommunicating
| Modulating ERV Setpoints | Can't Test | ERV Min Voltage | Setpoint |  |  | Working |  | test/topic/erv_type_modulating_0v | [7 empty] | vdc
|  | Can't Test | ERV Max Voltage | Setpoint |  |  | Working |  | test/topic/erv_type_modulating_10v | [7 empty] | vdc
Disables | ERV Disables | Dev and passed testing | Economizer | Radio Button | n |  | Working |  | cfg/i/heatWheel/enableMethod | EconoAtMin
|  | Dev and passed testing | OA Enthalpy | Radio Button | y |  | Working |  | cfg/i/heatWheel/enableMethod | OAEnthalpy |  |  |  |  | Must configure Digital or BACnet OA Sensor
| ERV OA Enthalpy Setpoints | Dev and passed testing | Low OA Enthalpy Setpoint | Setpoint |  |  | Working |  | sp/i/heatWheel/enable/outdoorEnthalpy/low | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | High OA Enthalpy Setpoint | Setpoint |  |  | Working |  | sp/i/heatWheel/enable/outdoorEnthalpy/high | {{float}} | [6 empty] | F or C
Bypass | ERV Bypass Type | Dev and passed testing | On/Off | Radio Button | n |  | Working |  | cfg/i/gc/fanConfig/heatWheel/ERVBypassType | OnOff
|  | Dev and passed testing | Modulating | Radio Button | y |  | Working |  | cfg/i/gc/fanConfig/heatWheel/ERVBypassType | Modulating
| Modulating ERV Bypass Setpoints | Dev and failed testing | OA ERV Bypass Min | Setpoint |  | UI label wrong | Working |  | cfg/i/gc/fanConfig/heatWheel/oaERVBypassMin | {{float}} | [6 empty] | vdc
|  | Dev and failed testing | Exhaust ERV Bypass Min | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/ExhaustERVBypassMin | {{float}} | [6 empty] | vdc
|  | Dev and failed testing | OA ERV Bypass Max | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/oaERVBypassMax | {{float}} | [6 empty] | vdc
|  | Dev and failed testing | Exhaust ERV Bypass Max | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/ExhaustERVBypassMax | {{float}} | [6 empty] | vdc
|  | Dev and passed testing | OA Differnetial Pressure | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/OADifferentialPressure | {{float}} | [6 empty] | "WG
|  | Dev and passed testing | Exhaust Differential Pressure | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/ExhaustDifferentialPressure | {{float}} | [6 empty] | "WG
Defrost | Defrost | Dev and passed testing | No Defrost | Radio Button | n |  | Working |  | cfg/i/gc/fanConfig/heatWheel/defrostEnabled | false
|  | Dev and passed testing | Defrost Enable | Radio Button | y |  | Working |  | cfg/i/gc/fanConfig/heatWheel/defrostEnabled | true
| ERV Defrost Setpoints | Dev and passed testing | OA Temperature | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/defrostTemp | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | OA Dewpoint | Setpoint |  |  | Working |  | cfg/i/gc/fanConfig/heatWheel/defrostDewpoint | {{float}} | [6 empty] | F or C

## Preheat
Section | Section | Page | Status | Feature | Type | Chevron? | QA Status | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Preheat Type | Preheat | Type | Dev and passed testing | None | Radio Button | n | Working | cfg/i/gc/heatConfig/preheatConfig/heatType | none
|  |  | Dev and passed testing | Electric | Radio Button | y | Working | cfg/i/gc/heatConfig/preheatConfig/heatType | electric
|  |  | Dev and passed testing | Water/Steam | Radio Button | y | Working | cfg/i/gc/heatConfig/preheatConfig/heatType | water
|  | Electric Setpoints | Dev and passed testing | Stage Up Window | Setpoint |  | Working | cfg/i/gc/heatConfig/preheatConfig/stageUpWindow | {{float}} | [6 empty] | F or C | 1 | 15 | 3
|  |  | Dev and passed testing | Stage Down Window | Setpoint |  | Working | cfg/i/gc/heatConfig/preheatConfig/stageDownWindow | {{float}} | [6 empty] | F or C | 1 | 15 | 3
|  |  | Dev and passed testing | Stage Up Timer | Setpoint |  | Working | cfg/i/gc/heatConfig/preheatConfig/stageUpTimerMinutes | {{int}} | [6 empty] | Min
|  |  | Dev and passed testing | Stage Down Timer | Setpoint |  | Working | cfg/i/gc/heatConfig/preheatConfig/stageDownTimerMinutes | {{int}} | [6 empty] | Min
|  | Water/Steam Setpoints | Dev and passed testing | Min Voltage | Setpoint |  | Working | cfg/i/gc/heatConfig/preheatConfig/minWaterVolts | {{float}} | [6 empty] | VDC
|  |  | Dev and passed testing | Max Voltage | Setpoint |  | Working | cfg/i/gc/heatConfig/preheatConfig/maxWaterVolts | {{float}} | [6 empty] | VDC
|  | Preheat Setpoints | Dev and passed testing | OAT Enable Setpoint | Setpoint |  | Working | sp/i/preheatEnableTemp | {{float}} | [6 empty] | F or C | -30 | 105 | 30
|  |  | Dev and passed testing | Cool Leaving Air Setpoint | Setpoint |  | Working | sp/i/preheat/LATSP/cool | {{float}} | [6 empty] | F or C | 0 | 90 | 45
|  |  | Dev and passed testing | Heat Leaving Air Setpoint | Setpoint |  | Working | sp/i/preheat/LATSP/heat | {{float}} | [6 empty] | F or C | 0 | 140 | 45
|  |  | Dev and passed testing | Vent Leaving Air Setpoint | Setpoint |  | Working | sp/i/preheat/LATSP/vent | {{float}} | [6 empty] | F or C | 0 | 90 | 45

## Heating
Section | Page | Status | Feature | Type | Chevron? | Topic Notes | QA Status | Dev comments | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Heating | Heat Type | Dev and failed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatType | none | cfg/i/gc/heatConfig/isHeatpump | false
|  | Dev and failed testing | Heat Pump | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/heatType | heatPump | cfg/i/gc/heatConfig/isHeatpump | true
|  | Dev and failed testing | Gas | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/heatType | gas | cfg/i/gc/heatConfig/isHeatpump | false
|  | Dev and failed testing | Heating Tempering | Child Checkbox | n |  | Working |  | cfg/i/manager/supplyAirTempering/enable | true
|  | Dev and failed testing | Electric | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/heatType | electric | cfg/i/gc/heatConfig/isHeatpump | false
|  | Dev and failed testing | Water/Steam | Radio Button | y | NYI | Working |  | cfg/i/gc/heatConfig/heatType | water | cfg/i/gc/heatConfig/isHeatpump | false
|  | Not Tested | Direct Fire | Radio Button | y | NYI | Working |  | cfg/i/gc/heatConfig/heatType | directFire | cfg/i/gc/heatConfig/isHeatpump | false
| Setpoints | Dev and passed testing | Stage Up Window | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/stageUpWindow | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Stage Down Window | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/stageDownWindow | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Stage Up Timer | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/stageUpTimerMinutes | {{int}} | [6 empty] | min
|  | Dev and passed testing | Stage Down Timer | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/stageDownTimerMinutes | {{int}} | [6 empty] | min
|  | Dev and passed testing | Min Run Time | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/minRunTime | {{int}} | [6 empty] | min
|  | Dev and passed testing | Min Off Time | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/minOffTime | {{int}} | [6 empty] | min
|  | Dev and passed testing | Heating OAT Lockout | Setpoint |  |  | Working |  | cfg/i/activeHeating/oatLockout | {{float} | [6 empty] | F or C
|  | Dev and passed testing | Heat SAT Setpoint | Setpoint |  |  | Working |  | sp/i/saTempHeatSP/max | {{float}} | [6 empty] | F or C |  |  | 150
|  | Dev and passed testing | High SAT Cutoff | Setpoint |  |  | Working |  | cfg/i/supplyAirTempCutoffHigh | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Heating Min Fan Speed | Setpoint |  |  | Working |  | cfg/i/SZVAV/fanHeatMinSpeed | {{float}} | [6 empty] | min
|  | Dev and passed testing | Heat Control Window | Setpoint |  |  | Working |  | cfg/i/manager/heating/controlWindow | {{float}} | [6 empty] | %
|  | Dev and passed testing | Heating Max Fan Speed | Setpoint |  |  | Working |  | cfg/i/SZVAV/fanHeatMaxSpeed | {{float}} | [6 empty] | %
|  | Dev and failed testing | Changeover Delay Time | Setpoint |  |  | Working |  | cfg/i/oppositeModeLockoutTime | {{float in seconds}}
Heat Pump | Type | Dev and failed testing | Air Source | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.heatPumpType | air
|  | Dev and passed testing | Water | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.heatPumpType | water
| WHP Glycol | Not Tested | 0% (32.0°F / 0°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 5% (29.1°F / -1.6°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 10% (26.1°F / -3.3°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 15% (22.9°F / -5.1°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 20% (19.2°F / -7.1°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 25% (14.7°F / -9.6°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 30% (9.2°F / -12.7°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 35% (2.4°F / -16.4°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Not Tested | 40% (-6.0°F / -21.1°C Freezing Point) | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
| Reversing Valve Type | Dev and failed testing | Fail to Heating | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.revValveFailTo | heat
|  | Dev and failed testing | Fail to Cooling | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.revValveFailTo | cool
| Aux/Emergency Heat | Dev and passed testing | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatType | none
|  | Dev and passed testing | Gas | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/heatType | gas
|  | Dev and failed testing | Heating Tempering | Child Checkbox | n |  | Working |  | cfg/i/manager/supplyAirTempering/enable | true
|  | Dev and passed testing | Aux Heat | Child Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/gasAsAux | true | [12 empty] | To be able to select this, the simultaneous heat/cool in Unit Settings must be enabled.
|  | Dev and passed testing | Emergency Heat | Child Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/gasAsAux | false | [12 empty] | To be able to select this, the simultaneous heat/cool in Unit Settings must be enabled.
|  | Dev and passed testing | Electric | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/heatType | electric
|  | Dev and passed testing | Water/Steam | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/heatType | water
| Gas - Heat Boards | Dev and failed testing | Heat Board 1 Unique ID | Button/Status |  |  | Working |  | cfg/i/gc/boards/heating/1/uuid | {{int}} | [12 empty] | Show number of boards selected in board section
|  | Dev and failed testing | Heat Board 2 Unique ID | Button/Status |  |  | Working |  | cfg/i/gc/boards/heating/2/uuid | {{int}} | [12 empty] | If not configured for 2 boards, do not show.
| Ignition Control Board 1 | Unknown
| Ignition Control Board 1 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/0/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/0/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/0/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | No UI to test | No topics and UI available
|  | Not Tested | Enables | Radio Button(s) | y | Where in the UI?? | No UI to test | No topics and UI available
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/0/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/0/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/0/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 2 | Unknown
| Ignition Control Board 1 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/1/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/1/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/1/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | No UI to test | No topics and UI available
|  | Not Tested | Enables | Radio Button(s) | y |  | No UI to test | No topics and UI available
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/1/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/1/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/1/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 3 | Unknown
| Ignition Control Board 3 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/2/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/2/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/2/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | No UI to test | No topics and UI available
|  | Not Tested | Enables | Radio Button(s) | y |  | No UI to test | No topics and UI available
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | Working | [15 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/2/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/2/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/2/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 4 | Unknown
| Ignition Control Board 4 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/3/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/3/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/3/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working
|  | Not Tested | Enables | Radio Button(s) | y |  | Working
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | Working | [15 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/3/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/3/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/3/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 5 | Unknown
| Ignition Control Board 5 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/4/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/4/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/4/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working
|  | Not Tested | Enables | Radio Button(s) | y |  | Working
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | Working | [15 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/4/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/4/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/4/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 6 | Unknown
| Ignition Control Board 6 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/5/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/5/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/5/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working
|  | Not Tested | Enables | Radio Button(s) | y |  | Working
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Not Tested | ModGas Valves Menu Button | Menu Button |  | For UI Only | Working | [15 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Not Tested | Valve 1 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Not Tested | Valve 2 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/5/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/5/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/5/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 7 | Unknown
| Ignition Control Board 7 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/6/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/6/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/6/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working
|  | Not Tested | Enables | Radio Button(s) | y |  | Working
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | Working | [15 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/6/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/6/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/6/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 8 | Unknown
| Ignition Control Board 8 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/7/modulatingEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/7/modulatingEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/7/modulatingEnables | 2
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working
|  | Not Tested | Enables | Radio Button(s) | y |  | Working
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board. Gray out option and throw validation message if they try to select it
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | Working | [15 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button |  |  | Working | [15 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only | Working |  | ui/heating/1/ignitionController/7/fixedEnables | none
|  | Not Tested | 1 Enable | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/7/fixedEnables | 1
|  | Not Tested | 2 Enables | Radio Button | y |  | Working |  | ui/heating/1/ignitionController/7/fixedEnables | 2
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
Unknown
| Electric - Heat Boards | Not Tested | Heat Board 1 Unique ID | Menu Button |  |  | Working |  | cfg/i/gc/boards/heating/1/uuid | {{int}}
|  | Not Tested | Heat Board 2 Unique ID | Menu Button |  |  | Working |  | cfg/i/gc/boards/heating/2/uuid | {{int}}
| Heat Enable Mouts | Unknown | Mouts (PLEASE READ NOTES) | Menu Button(s) | [18 empty] | From Heating board, if there are no heat enables, BUT an SCR Signal exists, then show the SCR Signal Mout. However, if there are heat enables, then DO NOT show the SCR Signal Mout option.
| Mout # - Enable | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | none
|  | Not Tested | SCR Enable | Radio Button | y | PinLocation, point to this MOUT | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/isSCR | true | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
|  | Not Tested | Fixed Enable | Radio Button | y |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/isSCR | false | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
| Mout # - SCR Enable | Not Tested | Aux Heat | Checkbox | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/auxHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
|  | Not Tested | Emergency Heat | Checkbox | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/emergencyHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
| Mout # - Fixed Enable | Not Tested | Aux Heat | Checkbox | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/auxHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
|  | Not Tested | Emergency Heat | Checkbox | n |  | Working |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/emergencyHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
| Water/Steam | Not Tested | Min Voltage | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/waterMinVolts | {{float}} | [6 empty] | VDC |  |  | 0
|  | Not Tested | Max Voltage | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/waterMaxVolts | {{float}} | [6 empty] | VDC |  |  | 10
| Heat Pump Setpoints | Not Tested | Aux Off Delay | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOffTime | {{int}} | [6 empty] | min
|  | Not Tested | Aux On Delay | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOnTime | {{int}} | [6 empty] | min
|  | Not Tested | Aux Off Window | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOffWindow | {{float}} | [6 empty] | F or C
|  | Not Tested | Aux On Window | Setpoint |  |  | Working |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOnWindow | {{float}} | [6 empty] | F or C
|  | Not Tested | Heat Pump OAT Lockout | Setpoint |  |  | Working |  | cfg/i/heatPump/minOutdoorAirTemp | {{float}} | [6 empty] | F or C
|  | Not Tested | Heat Superheat Setpoint | Setpoint |  |  | No UI to test | Working | cfg/i/superheatSP | {{float}}
Gas | Heat Boards | Not Tested | Heat Board 1 Unique ID | Menu Button |  |  | Working |  | cfg/i/gc/boards/heating/1/uuid | {{int}}
|  | Not Tested | Heat Board 2 Unique ID | Menu Button |  |  | Working |  | cfg/i/gc/boards/heating/2/uuid | {{int}}
| Ignition Control Board 1 | Unknown
| Ignition Control Board 1 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only | Working
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 2 | Unknown
| Ignition Control Board 1 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  | Working |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 3 | Unknown
| Ignition Control Board 3 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 4 | Unknown
| Ignition Control Board 4 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 5 | Unknown
| Ignition Control Board 5 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 6 | Unknown
| Ignition Control Board 6 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 7 | Unknown
| Ignition Control Board 7 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 8 | Unknown
| Ignition Control Board 7 | Not Tested | None | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | none
|  | Not Tested | Modulating | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | modulating
|  | Not Tested | Fixed | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | fixed
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Modulating - Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | Enables | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board. Gray out option and throw validation message if they try to select it
| Modulating - Valves | Unknown | ModGas Valves Menu Button | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Tested | Disable | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | false
|  | Not Tested | Enable | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | true
| Fixed Enables | Not Tested | None | Radio Button | n | For UI Only
|  | Not Tested | 1 Enable | Radio Button | y
|  | Not Tested | 2 Enables | Radio Button | y
| Fixed Heat 1 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
Unknown
Electric | Boards | Unknown | Heat Board 1 | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/1/uuid | {{int}}
|  | Unknown | Heat Board 2 | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/2/uuid | {{int}}
| Heat Enable Mouts | Unknown | Mout(s) | Menu Button(s) | [18 empty] | From Heating board, if there are no heat enables, BUT an SCR Signal exists, then show the SCR Signal Mout. However, if there are heat enables, then DO NOT show the SCR Signal Mout option.
| Mout Enable | Not Tested | None | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | none
|  | Not Tested | SCR Enable | Radio Button | n | replace heating/1/MOUT/5 with the pin location of this Mout |  |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/isSCR | true | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
|  | Not Tested | Fixed Enable | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/isSCR | false | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
Water/Steam | Water/Steam | Not Tested | Min Voltage | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/waterMinVolts | {{float}} | [6 empty] | VDC |  |  | 0
|  | Not Tested | Max Voltage | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/waterMaxVolts | {{float}} | [6 empty] | VDC |  |  | 10

## Cooling
Section | Page |  | Feature | Type | Chevron? | Topic Notes | QA Status | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Cooling | Circuit Menu | Not Tested | Circuit A | Menu Button |  |  |  | Just buttons | [13 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit B | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit C | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit D | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit E | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit F | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit G | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Not Tested | Circuit H | Menu Button | [17 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
| Setpoints | Not Tested | Stage Up Window | Setpoint |  |  | Working | cfg/i/manager/cooling/stageUpWindow
|  | Not Tested | Stage Down Window | Setpoint |  |  | Working | cfg/i/manager/cooling/stageDownWindow
|  | Not Tested | Stage Up Timer | Setpoint |  |  | Working | cfg/i/manager/cooling/stageUpTime
|  | Not Tested | Stage Down Timer | Setpoint |  |  | Working | cfg/i/manager/cooling/stageDownTime
|  | Not Tested | Minimum Run Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/minRunTimeMinutes
|  | Not Tested | Minimum Off Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/minOffTimeMinutes
|  | Not Tested | Cooling OAT Lockout | Setpoint |  |  | Working | cfg/i/dxCool/oatLockout
|  | Not Tested | Cool SAT Setpoint | Setpoint |  |  | Working | sp/i/saTempCoolSP/min
|  | Not Tested | Low SAT Cutoff | Setpoint |  |  | Working | cfg/i/supplyAirTempCutoffLow
|  | Not Tested | Cool Min Fan Speed | Setpoint |  |  | Working | cfg/i/SZVAV/fanCoolMinSpeed
|  | Not Tested | Cool Control Window | Setpoint |  |  | Working | cfg/i/manager/cooling/controlWindow
|  | Not Tested | Cool Superheat Setpoint | Setpoint |  |  | Working | cfg/i/superheatSP
|  | Not Tested | Changeover Delay Time | Setpoint |  |  | Working | cfg/i/oppositeModeLockoutTime
Circuit A | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitA/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitA/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitA/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitA/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitA/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitA/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitA/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit B | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitB/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitB/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitB/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitB/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitB/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitB/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitB/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit C | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitC/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitC/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitC/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitC/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitC/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitC/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitC/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit D | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitD/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitD/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitD/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitD/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitD/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitD/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitD/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit E | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitE/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitE/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitE/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitE/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitE/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitE/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitE/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit F | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitF/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitF/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitF/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitF/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitF/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitF/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitF/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit G | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitG/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitG/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitG/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitG/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitG/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitG/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitG/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit H | Compressor(s) | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/compressors[0] | none
|  | Not Tested | Cooling Board x, Refrigeration x, x Compressor | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitH/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Not Tested | Tandem Compressor (2) | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/circuitH/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Tested | None | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Tested | Power-Comm Board x, Comm x, EXV x | Radio Button | y |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Tested | Superheat Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Tested | Startup Disable Time | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Tested | Discharge Line Temp Setpoint | Setpoint |  |  | Working | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Tested | AHU Board 1, VFD Port x | Checkbox | n | The array needs to contain all the selected condenser fans | Working | cfg/i/gc/refrigConfig/circuitH/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/indoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/outdoorEXV | {{EXVLocation}}
|  | Not Tested | Power-Comm Board x, Port x, X EXV # | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/reversingValve | {{PinLocation}}
|  | Not Tested | AHU Board x, Mout X | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/reheatValve | {{PinLocation}}
|  | Not Tested | Cooling Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Not Tested | AHU Board x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Tested | None | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitH/proofOfWater | {{PinLocation}}
|  | Not Tested | Cooling Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitH/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Tested | AHU Board x, Binary Input x | Radio Button | n |  | NA | cfg/i/gc/refrigConfig/circuitH/proofOfWater | {{PinLocation}}
| Defrost | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/defrostSwitch | {{PinLocation}}
|  | Not Tested | AHU Board x, Binary Inut x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Not Tested | None | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/startupSolenoid | {{PinLocation}}
|  | Not Tested | Cooling Board x, Mout x | Radio Button | n |  | Working | cfg/i/gc/refrigConfig/circuitH/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"

## Fans
Section | Page | Status | Feature | Type | Chevron? |  | QA Status | QA Comments | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Supply Fans | Supply Fan Config | Dev and passed testing | CAV | Radio Button | n |  |  | Working | cfg/i/manager/supplyFan/controlMode | CAV
|  | Dev and passed testing | Filter Loading | Child Checkbox | y |  |  | Working | cfg/i/supplyFan/filterLoading | true
|  | Dev and passed testing | SZVAV | Radio Button | y |  | Working | Working | cfg/i/manager/supplyFan/controlMode | Sequence
|  | Dev and passed testing | Building Pressure | Radio Button | y |  | Working | Working | cfg/i/manager/supplyFan/controlMode | ModBuildingPressure | [12 empty] | Chevron goes to bldg pr workflow
|  | Not Tested | Controls Min OA | Radio Button | y |  | Working | Working | cfg/i/manager/supplyFan/controlMode | ControlsMinOA
|  | Dev and passed testing | Duct Static Control | Radio Button | y |  | Working | Working | cfg/i/manager/supplyFan/controlMode | ModStaticPressure
|  | Dev and passed testing | Has Static Reset | Child Checkbox | y |  | Working | Working | cfg/i/manager/ductStaticControl/staticReset/enable | true
|  | Dev and failed testing | Supply Fan Cycles w/ Heat/Cool | Checkbox | n | The logic on this point is reversed from the way it is written in the UI. Fan cycling would be occRunFan = false, and default behavior would be true | Working | Working | cfg/i/occRunFan | boolean |  |  |  |  | Unit MUST be in standard mode
|  | Dev and failed testing | SF runs while Unoccupied | Checkbox | y |  | Working | Working | cfg/i/unoccRunFan | boolean | [12 empty] | Gray out the chevron button if Duct Static Pressure is selected
| Filter Loading SP's | Dev and passed testing | Duct Static Setpoint | Setpoint |  |  | Working | Working | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the supply fan. The supply fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and passed testing | Duct Static Deadband | Setpoint |  |  | Working | Working | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.1 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
| SZVAV Setpoints | Dev and passed testing | Heat Min VFD | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanHeatMinSpeed | integer | [6 empty] | % | 0 | 100
|  | Dev and passed testing | Heat Max VFD | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanHeatMaxSpeed | integer | [6 empty] | % | 0 | 100
|  | Dev and passed testing | Cool Min VFD | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanCoolMinSpeed | integer | [6 empty] | % | 0 | 100
| Duct Static SP's | Dev and passed testing | Duct Static Setpoint | Setpoint |  |  | Working | Working | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the supply fan. The supply fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and passed testing | Duct Static Deadband | Setpoint |  |  | Working | Working | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.1 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
| Static Reset SP's | Dev and passed testing | Minimum | Setpoint |  |  | Working | Working | cfg/i/manager/ductStaticControl/staticReset/min | [7 empty] | % | 0 | 100
| Global SF Setpoints | Dev and passed testing | Cool Min Speed | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanCoolMinSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | Vent Speed | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanVentMinSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | Heat Min Speed | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanHeatMinSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | Heat Max Speed | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanHeatMaxSpeed | [7 empty] | % | 0 | 100
|  | Dev and failed testing | # of Allowed Fan Failures | Setpoint |  | We're missing this setpoint for return and exhaust fans | Working | Working | cfg/i/gc/fanConfig/numAllowedSupplyFanFailures | integer
| SF During Unoccupied Mode | Dev and passed testing | Fixed Speed | Setpoint |  |  | Working | Working | cfg/i/SZVAV/fanUnocc/fixedSpeed | integer | [6 empty] | % | 0 | 100
Return Fan | Config | Can't Test | CAV (Default) | Radio Button | n |  |  | No Topic | test/topic/fans_return_cav | ReturnFansCAV
|  | Can't Test | Building Pressure Control | Radio Button | y |  |  | No Topic | test/topic/fans_return_building_pressure | returnFansBP | [12 empty] | Navigates to Building Pressure workflow
| Allowed Fails | Can't Test | Number of allowed fan failures | Setpoint |  |  |  | No UI | cfg/i/gc/fanConfig/numAllowedReturnFanFailures
Exhaust Fan | Config | Can't Test | CAV (Default) | Radio Button | n |  |  | No Topic | test/topic/fans_exhaust_cav | exhaustFansCAV
|  | Can't Test | Building Pressure Control | Radio Button | y |  |  | No Topic | test/topic/fans_exhaust_building_pressure | exhaustFansBP | [12 empty] | Navigates to Building Pressure workflow
| Allowed Fails | Can't Test | Number of allowed fan failures | Setpoint |  |  |  |  | cfg/i/gc/fanConfig/numAllowedReturnFanFailures
No Reheat | Radio Button | n | cfg/i/refrig/reheat/additionalSource
Modulating HGR | Radio Button | y
No Additional Reheat | Child Radio | n | cfg/i/refrig/reheat/additionalSource
Plus Aux Heat (Heat Pump Required) | Child Radio | n | cfg/i/refrig/reheat/additionalSource
Plus Unit Heat (call factory) | Child Radio | y | cfg/i/refrig/reheat/additionalSource
Unit Heat for Reheat | Radio Button | n | cfg/i/refrig/reheat/additionalSource