## Progression
Status | Unit Settings | Unit Settings -Boards | AHU | Sensors | OA Dampers | Dehum | Filters | Building Pressure | ERV | Preheat | Heating | Cooling | Fans | Status | Total
Not Developed | 56 | 448 | 15 | 9 | 0 | 2 | 0 | 4 | 0 | 0 | 34 | 0 | 0 | Not Developed | 512
Dev and Passed Testing | 17 | 666 | 1027 | 24 | 18 | 0 | 0 | 31 | 18 | 13 | 136 | 37 | 20 | Dev and Passed Testing | 1990
Dev and Failed Testing | 14 | 254 | 34 | 4 | 4 | 20 | 0 | 0 | 0 | 0 | 108 | 40 | 2 | Dev and Failed Testing | 466
Dev and Partial Tested | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Dev and Partial Tested | 0
Can't Dev/Test | 31 | 17 | 0 | 0 | 0 | 14 | 60 | 6 | 4 | 0 | 32 | 0 | 6 | Can't Dev/Test | 139
Dev and Not tested | 4 | 180 | 0 | 4 | 0 | 3 | 0 | 0 | 0 | 0 | 160 | 0 | 1 | Dev and Not tested | 348
Total | 66 | 1117 | 1061 | 32 | 22 | 37 | 60 | 37 | 22 | 13 | 436 | 77 | 29 | 3141

## Progression 1.0
Status | Unit Settings | Unit Settings -Boards | AHU | Sensors | OA Dampers | Dehum | Building Pressure | ERV | Preheat | Heating | Cooling | Fans | Status | Total
Not Developed | 56 | 448 | 15 | 9 | 0 | 2 | 4 | 0 | 0 | 34 | 0 | 0 | Not Developed | 512
Dev and Passed Testing | 17 | 666 | 1027 | 24 | 18 | 0 | 31 | 18 | 13 | 136 | 37 | 20 | Dev and Passed Testing | 1990
Dev and Failed Testing | 14 | 254 | 34 | 4 | 4 | 20 | 0 | 0 | 0 | 108 | 40 | 2 | Dev and Failed Testing | 466
Dev and Partial Tested | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Dev and Partial Tested | 0
Can't Dev/Test | 31 | 17 | 0 | 0 | 0 | 14 | 6 | 4 | 0 | 32 | 0 | 6 | Can't Dev/Test | 79
Dev and Not tested | 4 | 180 | 0 | 4 | 0 | 3 | 0 | 0 | 0 | 160 | 0 | 1 | Dev and Not tested | 348

## Change Logs
Version | Change notes | Location
1.1.6 | 1. Low and High Tolerance to be subscribed with cfg/i/spaceControl/season to determine what second topic to subscrbe and publish to. 2. Plus Aux Heat (Heat Pump Required) and Plus Unit Heat (call factory) changed from checkbox to radial. Added "no additional Reheat" child radial 3. Boards changed to individual Topics rather than 1 json | 1. Unit Settings -> Space Control (Precision) -> Manual Setpoints AND Auto Season Setpoints 2 2. Dehum -> Reheat 3. Unit Settings - boards -> Boards
1.1.7 | 1. Add UUID Payload. 2. true/false in temp scale converted to lowercase. 3. added overrideActive in AHU Mout's | 1. UUID in boards. 2. Unit Settings -> Scales 3. AHU ->AHU Mouts
1.1.8 | 1. Changed Plus Humidity to Child CheckBox 2. Modulating - Enables, Fixed Enables updated with UI topics | 1. Sensors, Row 19 and 24 2. Heating
1.1.9 | 1. Added UI Topics for needed locations. Will need to add for rest on later date. 2. Changed payload for UUID from "uuid" to "sn": | Unit Settings, Unit Setting - Boards, Dehum, Building Pressure, Heating
1.2.0 | 1. Added "Updated Topics 5-29 to 6-9" for CD to analyze changes to topics | Updated Topics 5-29 to 6-9

## Updated Topics 5-29 to 6-9
Updated File | File Line | Topic or Key | Payloads | Dev Status | Dev Comments | 5
mqttTopicsConfig.constans.ts | 8899 | ui/cfg/unitSettings/appType |  | Completed
dynamicFormMenus.constants.ts | 6073 | StorageKeys.AIR_HANDLER_ANALOG_SUPPY_FAN | analogSupplyFan | Completed
dynamicFormMenus.constants.ts | 6083 | StorageKeys.AIR_HANDLER_ANALOG_RETURN_FAN | analogReturnFan | Completed
dynamicFormMenus.constants.ts | 6093 | StorageKeys.AIR_HANDLER_ANALOG_EXHAUST_FAN | analogExhaustFan | Completed
dynamicFormMenus.constants.ts | 6013 | StorageKeys.AIR_HANDLER_ANALOG_CONDENSER_FAN | analogCondenserFan | Completed
dynamicFormMenus.constants.ts | 665 | AHU_CRANK_CASE_HEATER | ahuCrankCaseHeater | Completed
dynamicFormMenus.constants.ts | 662 | TelemetryLabel.UI_UNIT_SETTINGS_APP_TYPE | outdoorAirControl | Completed
dynamicFormMenus.constants.ts | 648 | TelemetryLabel.UI_UNIT_SETTINGS_APP_TYPE | supplyAirControl | Completed
dynamicFormMenus.constants.ts | 679 | TelemetryLabel.UI_UNIT_SETTINGS_APP_TYPE | returnAirControl | Completed
dynamicFormMenus.constants.ts | 685 | TelemetryLabel.APP_TYPE_MAIN_SEQUENCE, | SpaceControlDemandSZVAV | Completed
dynamicFormMenus.constants.ts | 685 | TelemetryLabel.USE_RETURN_OVER_SPACE_TEMP | true | Completed
dynamicFormMenus.constants.ts | 694 | UI_UNIT_SETTINGS_APP_TYPE | thirdParty | Completed
dynamicFormMenus.constants.ts | 4880 | TelemetryLabel.POWERCOMM_COMM | none | Completed
dynamicFormMenus.constants.ts | 4880 | TelemetryLabel.POWER_COMM_EXV1_TYPE | none | Completed
dynamicFormMenus.constants.ts | 4887 | TelemetryLabel.POWERCOMM_COMM | sporlan | Completed
dynamicFormMenus.constants.ts | 4887 | TelemetryLabel.POWER_COMM_EXV1_TYPE | sporlan | Completed
dynamicFormMenus.constants.ts | 4916 | TelemetryLabel.POWERCOMM_COMM | sanhua | Completed
dynamicFormMenus.constants.ts | 4916 | TelemetryLabel.POWER_COMM_EXV1_TYPE | sanhua | Completed
mqttTopicsConfig.constants.ts | 7278 | ${configInbandCommunication}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.BOARDS}/${MQTTTopicsPath.COOLING}/\${${ConfigNavigationType.BOARD}}/${MQTTTopicsPath.VFD}/\${${ConfigNavigationType.REFRIGERATION}}/\${${ConfigNavigationType.COMPRESSOR_TOPIC}}/${MQTTTopicsPath.TYPE} | only changed topic pathing | Completed
mqttTopicsConfig.constants.ts | 7285 | ${configInbandCommunication}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.BOARDS}/${MQTTTopicsPath.COOLING}/\${${ConfigNavigationType.BOARD}}/${MQTTTopicsPath.VFD}/\${${ConfigNavigationType.REFRIGERATION}}/\${${ConfigNavigationType.COMPRESSOR_TOPIC}}/${MQTTTopicsPath.MAKE} | only changed topic pathing | Completed
mqttTopicsConfig.constants.ts | 7293 | ${configInbandCommunication}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.BOARDS}/${MQTTTopicsPath.COOLING}/\${${ConfigNavigationType.BOARD}}/${MQTTTopicsPath.VFD}/\${${ConfigNavigationType.REFRIGERATION}}/\${${ConfigNavigationType.COMPRESSOR_TOPIC}}/${MQTTTopicsPath.RUNASANALOG} | only changed topic pathing | Completed
mqttTopicsConfig.constants.ts | 7301 | ${configInbandCommunication}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.BOARDS}/${MQTTTopicsPath.COOLING}/\${${ConfigNavigationType.BOARD}}/${MQTTTopicsPath.VFD}/\${${ConfigNavigationType.REFRIGERATION}}/\${${ConfigNavigationType.COMPRESSOR_TOPIC}}/${MQTTTopicsPath.MODEL} | only changed topic pathing | Completed
mqttTopicsConfig.constants.ts | 7309 | ${configInbandCommunication}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.BOARDS}/${MQTTTopicsPath.COOLING}/\${${ConfigNavigationType.BOARD}}/${MQTTTopicsPath.VFD}/\${${ConfigNavigationType.REFRIGERATION}}/\${${ConfigNavigationType.COMPRESSOR_TOPIC}}/${MQTTTopicsPath.VOLTAGE} | only changed topic pathing | Completed
dynamicFormMenus.constants.ts | 1054 | TelemetryLabel.FAHRENHEIT_OR_CELSIUS | false | Completed
dynamicFormMenus.constants.ts | 1062 | TelemetryLabel.FAHRENHEIT_OR_CELSIUS | true | Completed
dynamicFormMenus.constants.ts | 3066 | TelemetryLabel.HEATING_TYPE_NONE | none | Completed
dynamicFormMenus.constants.ts | 3066 | TelemetryLabel.HEATING_CONFIG_HEATPUMP | false | Completed
dynamicFormMenus.constants.ts | 3080 | TelemetryLabel.HEATING_CONFIG_HEATPUMP | true | Completed
dynamicFormMenus.constants.ts | 3082 | TelemetryLabel.HEATING_TYPE_UI | only changed topic pathing | Completed
dynamicFormMenus.constants.ts | 3082 | TelemetryLabel.HEATING_TYPE_NONE | gas | Completed
dynamicFormMenus.constants.ts | 3121 | TelemetryLabel.HEATING_TYPE_NONE | electric | Completed
dynamicFormMenus.constants.ts | 3137 | TelemetryLabel.HEATING_TYPE_NONE | water | Completed
mqttTopicsConfig.constants.ts | 9040 | cfg/i/gc/heatConfig/isHeatPump | only changed topic pathing | Completed
mqttTopicsConfig.constants.ts | 9032 | ui/config/heatConfig/heatType | only changed topic pathing | Completed
dynamicFormMenus.constants.ts | 3369 | TelemetryLabel.GAS_AS_AUX | true | Completed
mqttTopicsConfig.constants.ts | 2609 | cfg/i/heatPump/minOutdoorAirTemp | only changed topic pathing | Completed
mqttTopicsConfig.constants.ts | 6432 | cfg/i/gc/heatConfig/heatPumpConfig.heatPumpType |  | Completed
coolingCircuitsCondensorFanMenuGenerator.ts | 19 | cfg/i/gc/boards/airHandler/{board}/VFD/{vfd}/selection |  | Completed
coolingCircuitsCondensorFanMenuGenerator.ts | 22 | cfg/i/gc/refrigConfig/circuitA/condenserFans |  | Yet to start | topic commented
coolingCircuitsCondensorFanMenuGenerator.ts | 25 | airHandler/${board}/VFD/${vfd} |  | Completed
coolingCircuitsInsideexvMenuGenerator | 49 | cfg/i/gc/boards/powerComm/{board}/uuid |  | Completed
coolingCircuitsOutsideexvMenuGenerator | 27 | input.match( /powerComm\/(\d+)\/EXVComm\/(\d+)\/sporlan\/exv(\d+)\/location/ |  | Completed
coolingCircuitsReheatvalveMenuGenerator | 15 | cfg/i/gc/boards/cooling/{board}/ReheatValve/1/selection |  | Yet to start | complete flow of reheat is changed in prodev branch
coolingCircuitsReheatvalveMenuGenerator | 16 | cfg/i/gc/boards/cooling/{board}/uuid |  | Completed
coolingCircuitsReversingvalveMenuGenerator | 34 | cfg/i/gc/boards/cooling/{board}/uuid |  | Yet to start | As per figjam reversing valve only enables when the air handler board is configured, need to accomodate cooling board configurations as well
coolingCircuitsReversingvalveMenuGenerator | 35 | cfg/i/gc/boards/airHandler/{board}/uuid |  | Completed
coolingCircuitsSolenoidMenuGenerator | 28 | cfg/i/gc/boards/cooling/{board}/uuid |  | Completed
coolingCompressorVaporMenuGenerator | 33 | cfg/i/gc/boards/powerComm/{board}/uuid |  | Completed
coolingCompressorVaporMenuGenerator | 53 | powerComm/${board}/EXVComm/${comm} |  | Completed
dynamicFormMenus.constants.ts | 4973 | TelemetryLabel.POWER_COMM_EXV1_TYPE | none | Yet to start
dynamicFormMenus.constants.ts | 4973 | TelemetryLabel.POWER_COMM_EXV_SELECTION | none | Completed
dynamicFormMenus.constants.ts | 4986 | TelemetryLabel.POWER_COMM_EXV1_TYPE | sporlan | Yet to start
dynamicFormMenus.constants.ts | 4986 | TelemetryLabel.POWER_COMM_EXV_SELECTION | sporlan | Completed
dynamicFormMenus.constants.ts | 5000 | TelemetryLabel.POWER_COMM_EXV1_TYPE | sporlanVI | Yet to start | telementry not available
dynamicFormMenus.constants.ts | 5000 | TelemetryLabel.POWER_COMM_EXV_SELECTION | sporlanVI | Completed
dynamicFormMenus.constants.ts | 5015 | TelemetryLabel.POWER_COMM_EXV1_TYPE | sanhua | Yet to start | telementry not available
dynamicFormMenus.constants.ts | 5015 | TelemetryLabel.POWER_COMM_EXV_SELECTION | sanhua | Completed | Used as 2nd topic against topicKey: TelemetryLabel.POWER_COMM_UI_EXV1
mqttTopicsConfig.constants.ts | 5485 | StorageKeys.AHU_BINARY_WATER_PROOF | proofOfH2O | Completed | Used In dynamicFormMenus.constants.ts
heatingEnablesMenuGenerators | 23 | TelemetryLabel.UI_EHS_ENABLE |  | Completed | Used In heatingEnablesMoutsMenuGenerators
heatingEnablesMenuGenerators | 35 | TelemetryLabel.UI_EHS_ENABLE |  | Completed | Used In heatingEnablesMoutsMenuGenerators
heatingEnablesMenuGenerators | 45 | TelemetryLabel.UI_EHS_ENABLE |  | Completed | Used In heatingEnablesMoutsMenuGenerators
mqttTopicsConfig.constants.ts | 4929 | ${MQTTTopicsPath.PLACEHOLDER_TOPIC_1}${stringUtlis.toLowerCaseWithNoSpaces(this.key)} |  | Completed
mqttTopicsConfig.constants.ts | 7078 | ${MQTTTopicsPath.CONFIG}/${MQTTTopicsPath.I}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.REFRIGCONFIG}/${MQTTTopicsPath.COOLING}/1/${MQTTTopicsPath.VFD}/1/${MQTTTopicsPath.COMPRESSOR2}/${MQTTTopicsPath.VI}/${MQTTTopicsPath.SUPERHEATSP} |  | Completed
mqttTopicsConfig.constants.ts | 7089 | ${MQTTTopicsPath.CONFIG}/${MQTTTopicsPath.I}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.REFRIGCONFIG}/${MQTTTopicsPath.COOLING}/1/${MQTTTopicsPath.VFD}/1/${MQTTTopicsPath.COMPRESSOR2}/${MQTTTopicsPath.VI}/${MQTTTopicsPath.STARTUPDISABLEDTIMEMINUTES} |  | Completed
mqttTopicsConfig.constants.ts | 7100 | ${MQTTTopicsPath.CONFIG}/${MQTTTopicsPath.I}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.REFRIGCONFIG}/${MQTTTopicsPath.COOLING}/1/${MQTTTopicsPath.VFD}/1/${MQTTTopicsPath.COMPRESSOR2}/${MQTTTopicsPath.VI}/${MQTTTopicsPath.DISCHARGEINETEMPSP} |  | Completed
coolingCircuitsCondensorFanMenuGenerator | 21 | cfg/i/gc/refrigConfig/circuitA/condenserFanCooling |  | Yet to start | commented topic in client branch
dynamicFormMenus.constants.ts | 3334 | TelemetryLabel.UI_EMER_HEAT_TYPE |  | Completed
dynamicFormMenus.constants.ts | 3345 | TelemetryLabel.UI_EMER_HEAT_TYPE |  | Completed
dynamicFormMenus.constants.ts | 3362 | topicKey: TelemetryLabel.UI_EMER_GAS_AS_AUX |  | Completed
dynamicFormMenus.constants.ts | 3375 | TelemetryLabel.UI_EMER_GAS_AS_AUX |  | Yet to start
dynamicFormMenus.constants.ts | 3392 | TelemetryLabel.UI_EMER_HEAT_TYPE |  | Completed
mqttTopicsConfig.constants.ts | 416 | ${MQTTTopicsPath.SP}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.DUCT_STATIC_PRESSURE_SP} |  | Completed
mqttTopicsConfig.constants.ts | 2616 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/heatPump/minOutdoorAirTemp |  | Completed
mqttTopicsConfig.constants.ts | 3555 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SPACE_CONTROL}/${MQTTTopicsPath.SEASON_CHANGE_OVER}/${MQTTTopicsPath.AUTO} |  | Completed
mqttTopicsConfig.constants.ts | 3561 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SPACE_CONTROL}/${MQTTTopicsPath.SEASON_CHANGE_OVER}/${MQTTTopicsPath.AUTO} |  | Completed
mqttTopicsConfig.constants.ts | 3567 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.ENABLE} |  | Completed
mqttTopicsConfig.constants.ts | 3573 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.ENABLE} |  | Completed
mqttTopicsConfig.constants.ts | 3596 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.SOURCE} |  | Completed
mqttTopicsConfig.constants.ts | 3602 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.SOURCE} |  | Completed
mqttTopicsConfig.constants.ts | 3608 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.SOURCE} |  | Completed
mqttTopicsConfig.constants.ts | 3614 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.SOURCE} |  | Completed
mqttTopicsConfig.constants.ts | 3620 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.MANAGER}/${MQTTTopicsPath.SAT_RESET}/${MQTTTopicsPath.SOURCE} |  | Completed
mqttTopicsConfig.constants.ts | 3802 | ${MQTTTopicsPath.SP}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.OCCUPIED_COOLING_SETPOINT} |  | Completed | Changed based on mastersheet
mqttTopicsConfig.constants.ts | 3811 | ${MQTTTopicsPath.SP}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.OCCUPIED_HEATING_SETPOINT} |  | Completed | Changed based on mastersheet
mqttTopicsConfig.constants.ts | 3834 | ${MQTTTopicsPath.SP}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.IAQ} |  | Completed
mqttTopicsConfig.constants.ts | 3980 | ${MQTTTopicsPath.Property_CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SENSEL}/_/${MQTTTopicsPath.OUTSIDE_TEMP}/${MQTTTopicsPath.OVERRIDE} |  | Completed
mqttTopicsConfig.constants.ts | 3988 | ${MQTTTopicsPath.Property_CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SENSEL}/_/${MQTTTopicsPath.OUTSIDE_TEMP}/${MQTTTopicsPath.OVERRIDE} |  | Completed
mqttTopicsConfig.constants.ts | 3996 | ${MQTTTopicsPath.Property_CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SENSEL}/_/${MQTTTopicsPath.OUTSIDE_TEMP}/${MQTTTopicsPath.OVERRIDE} |  | Completed
mqttTopicsConfig.constants.ts | 4066 | ${MQTTTopicsPath.Property_CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SENSEL}/_/${MQTTTopicsPath.CO2}/${MQTTTopicsPath.EXISTS} |  | Completed
mqttTopicsConfig.constants.ts | 4072 | ${MQTTTopicsPath.Property_CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SENSEL}/_/${MQTTTopicsPath.CO2}/${MQTTTopicsPath.OVERRIDE} |  | Completed
mqttTopicsConfig.constants.ts | 4086 | ${MQTTTopicsPath.Property_CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.SENSEL}/_/${MQTTTopicsPath.CO2}/${MQTTTopicsPath.OVERRIDE} |  | Completed
mqttTopicsConfig.constants.ts | 4198 | ${MQTTTopicsPath.CONFIG}/${CommunicationMode.IN_BAND}/${MQTTTopicsPath.GC}/${MQTTTopicsPath.FAN_CONFIG}/${MQTTTopicsPath.HEATWHEEL}/${MQTTTopicsPath.CONTROLMETHOD} |  | Completed
displayMode.tsx | 41 | getTelemetryKey(TelemetryLabel.BACKLIGHT_UNIT_MANAGER) |  | Completed
timeContext | 48 | TelemetryLabel.STRATUS_TIME_CURRENT |  | Completed
DBExport | 8 | TelemetryLabel.DB_EXPORT |  | Completed
DBExport | 11 | TelemetryLabel.DB_RESPONSE |  | Completed
unitConfig | 287 | TelemetryLabel.APPLY_CONFIG |  | Completed
displayMode | 159 | BACKLIGHT_CONFIG.topic |  | Completed

## Unit Settings
Section | Page | Can't Test | Feature | Dev Changes | Dev Status | Type | Chevron? | UI Topics | UI Payloads | Topic | Payload | QA Testing - Dev build | Topic 2 (if required) | Payload 2 (if required) | QA Testing | Validation | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
App Type Selection | App Type | Dev and failed testing | Space Control | 1)Payloads - field value 2)topics - field value 3)Retain topic 1 & 2 | working | Radio Button | n | ui/cfg/unitSettings/appType | spaceAirControl | cfg/i/mainSequence | SpaceControlDemandSZVAV |  | cfg/i/spaceControl/useReturnOverSpaceTemp | false | [9 empty] | Aligned
|  | Dev and passed testing | Standard (Default) | Retained | working | Child Radio | y | ui/cfg/unitSettings/appType/spaceControl/mode | standard | cfg/i/spaceControl/mode | Eco | [12 empty] | Aligned
|  | Dev and passed testing | Precision | Retained | working | Child Radio | y | ui/cfg/unitSettings/appType/spaceControl/mode | precision | cfg/i/spaceControl/mode | Precision | [12 empty] | Aligned
|  | Dev and passed testing | VAV Control | 1)Payloads - field value 2)topics - field value | working | Radio Button | y | ui/cfg/unitSettings/appType | vav | cfg/i/mainSequence | SupplyAirControl | [12 empty] | Not Aligned
|  | Dev and passed testing | Outdoor Air Control | 1)Payloads - field value 2)topics - field value | working | Radio Button | y | ui/cfg/unitSettings/appType | outdoorAirControl | cfg/i/mainSequence | OutdoorAirControl | [12 empty] | Not for April
|  | Dev and passed testing | Has Return Air |  |  | Child Checkbox | y | ui/cfg/unitSettings/appType/hasReturnAir | boolean | pcfg/i/systemConfig/_/unitConfig/ahuProcess/hasReturnDucting | true/false
|  | Dev and failed testing | Return Air Control | 1)Payloads - field value 2)topics - field value 3)Retain topic 2 | working | Radio Button | y | ui/cfg/unitSettings/appType | returnAirControl | cfg/i/mainSequence | SpaceControlDemandSZVAV |  | cfg/i/spaceControl/useReturnOverSpaceTemp | true
|  | Can't Test | 3rd Party Interface | 1)UI Topic and payload - field value 2)Toipic 1 - cfg/i/mainSequence and it's payload - thirdParty | working | Radio Button | y | ui/cfg/unitSettings/appType | thirdParty | [6 empty] | Must Configure 3pi Board
|  | Dev and failed testing | Enable Unoccupied Setpoints |  |  | checkbox | y | ui/cfg/unitSettings/appType/enableUnoccupiedSetpoints | boolean | cfg/i/unoccTempControlEnable | true/false | [12 empty] | Not Aligned
Space Control (Standard) | Standard | Dev and passed testing | Occupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/occCoolSpaceTempSP | integer | [7 empty] | F or C
|  | Dev and passed testing | Occupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/occHeatSpaceTempSP | integer | [7 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Not Tested | Unoccupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | integer
|  | Not Tested | Unoccupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | integer
Night Setback | Night Setback Unoccupied Temps | Not Tested | Unoccupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | integer | [7 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Not Tested | Unoccupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | integer | [7 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
Space Control (Precision) | Precision Mode Type | Dev and passed testing | Manual (Default) |  |  | Radio Button | y |  |  | cfg/i/spaceControl/seasonChangeover/auto | false
|  | Dev and passed testing | Auto Season Changeover Enable |  |  | Radio Button | y |  |  | cfg/i/spaceControl/seasonChangeover/auto | true
| Manual Setpoints | Dev and passed testing | Occupied Space Temperature Setpoint | Retained | working | Setpoint |  |  |  | cfg/i/spaceControl/summerSP | integer | [7 empty] | F or C | -30 | 110 | 72 | This is the Mode Enable Setpoint that calls for Occupied Cooling Mode. When the HVAC mode enable source temperature is above this value will put the unit into cooling mode.
|  | Dev and passed testing | Unoccupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | integer | [7 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Dev and passed testing | Unoccupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | integer | [7 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Dev and failed testing | High Tolerance |  |  | Setpoint |  |  |  | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorHigh and pcfg/i/pid/summerDemand/_/accelerationBand/errorHigh | Integer |  | Check to see if cfg/i/spaceControl/season is in summer or winter, then publish to the corresponding topic. if noting is received, default to summer. |  |  | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint |  | Subscribe to first topic to descide which second topic to use.
|  | Dev and failed testing | Low Tolerance |  |  | Setpoint |  |  |  | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorLow and pcfg/i/pid/summerDemand/_/accelerationBand/errorLow | Integer |  | Check to see if cfg/i/spaceControl/season is in summer or winter, then publish to the corresponding topic. if noting is received, default to summer. |  |  | F or C | [5 empty] | Subscribe to first topic to descide which second topic to use.
| Auto Season Setpoints 1 | Dev and passed testing | Occupied Summer Setpoint |  |  | Setpoint |  |  |  | cfg/i/spaceControl/summerSP | Integer | [7 empty] | F or C
|  | Dev and passed testing | Occupied Winter Setpoint | Retained | working | Setpoint |  |  |  | cfg/i/spaceControl/winterSP | Integer | [7 empty] | F or C | -30 | 110 | 72
|  | Dev and failed testing | Unoccupied Heating Winter Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | Integer | [7 empty] | F or C | -30 | 110 |  | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Dev and failed testing | Unoccupied Cooling Winter Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | Integer | [7 empty] | F or C | -30 | 110 |  | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
|  | Dev and failed testing | Unoccupied Heating Summer Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | Integer | [7 empty] | F or C | -30 | 110
|  | Dev and failed testing | Unoccupied Cooling Summer Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | Integer | [7 empty] | F or C | -30 | 110
| Auto Season Setpoints 2 | Dev and failed testing | High Tolerance |  |  | Setpoint |  |  |  | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorHigh and pcfg/i/pid/summerDemand/_/accelerationBand/errorHigh | Integer |  |  |  |  | F or C
|  | Dev and failed testing | Low Tolerance |  |  | Setpoint |  |  |  | cfg/i/spaceControl/season | Winter OR Summer |  | pcfg/i/pid/winterDemand/_/accelerationBand/errorLow and pcfg/i/pid/summerDemand/_/accelerationBand/errorLow | Integer |  |  |  |  | F or C | -30 | 110 | 74
|  | Dev and passed testing | Summer Outdoor Air Enable Setpoint | Retained | working | Setpoint |  |  |  | cfg/i/spaceControl/seasonChangeover/summerOATemp | [8 empty] | F or C | -30 | 110 | 70
|  | Dev and passed testing | Winter Outdoor Air Enable Setpoint | Retained | working | Setpoint |  |  |  | cfg/i/spaceControl/seasonChangeover/winterOATemp | [8 empty] | F or C | -30 | 110 | 75
|  | Dev and failed testing | Season Changeover Time | Retained | working | Setpoint |  |  |  | cfg/i/spaceControl/seasonChangeover/time | 0-23 (AM and PM) | [7 empty] | Min | -30 | 110 | 55
|  | Dev and passed testing | Season Changeover Duration | Retained | working | Setpoint |  |  |  | cfg/i/spaceControl/seasonChangeover/successfulChecks/req | [8 empty] | Days
VAV Control | VAV - Config | Not Developed | Morning Warm Up | Retained topic 1 | working | Checkbox | y |  |  | cfg/i/manager/morningWarmup/enabled | boolean
|  | Not Developed | Morning Cool Down |  |  | Checkbox | y |  |  | cfg/i/manager/morningCooldown/enabled | boolean
|  | Not Developed | Enable Unit Heating |  |  | Checkbox | y |  |  | cfg/i/manager/vav/heatingEnabled | boolean
| Morning Warmup SP's | Not Developed | Return Air Temp | Retained | working | Setpoint |  |  |  | cfg/i/manager/morningWarmup/raSetpoint | float (degrees F)
|  | Not Developed | Time Period | Retained | working | Setpoint |  |  |  | cfg/i/manager/morningWarmup/duration | integer (minutes)
|  | Not Developed | Supply Air Heating | Retained | working | Setpoint |  |  |  | cfg/i/manager/morningWarmup/supplyAirSetpoint | float (degrees F)
| Morning Cooldown SP's | Not Developed | Return Air Temp | Retained | working | Setpoint |  |  |  | cfg/i/manager/morningCooldown/raSetpoint | float (degrees F)
|  | Not Developed | Time Period | Retained | working | Setpoint |  |  |  | cfg/i/manager/morningCooldown/duration | integer (minutes)
|  | Not Developed | Supply Air Heating | Retained | working | Setpoint |  |  |  | cfg/i/manager/morningCooldown/supplyAirSetpoint | float (degrees F)
| Unit Heating SP's | Not Developed | Cool OAT Enable Setpoint |  |  | Setpoint |  |  |  | sp/i/occCoolSpaceTempSP | float (degrees F)
|  | Not Developed | Heat OAT Enable Setpoint |  |  | Setpoint |  |  |  | sp/i/occHeatSpaceTempSP | float (degrees F)
| Duct Static Pressure Setpoint | Not Developed | Duct Static Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/ductStaticPressureSP | float (wg)
| VAV - SAT Reset | Not Developed | No SAT Reset |  |  | Radio Button | n |  |  | cfg/i/manager/satReset/enable | boolean
|  | Not Developed | Enable SAT Reset |  |  | Radio Button | y |  |  | cfg/i/manager/satReset/enable | boolean
| VAV - SAT Source Type | Not Developed | Outside Air |  |  | Radio Button | y |  |  | cfg/i/manager/satReset/source | OA
|  | Not Developed | Space Air |  |  | Radio Button | y |  |  | cfg/i/manager/satReset/source | Space
|  | Not Developed | Return Air |  |  | Radio Button | y |  |  | cfg/i/manager/satReset/source | Return
|  | Not Developed | Supply Fan VFD |  |  | Radio Button | y |  |  | cfg/i/manager/satReset/source | SupplyFanSpeed
|  | Not Developed | Remote Voltage Signal |  |  | Radio Button | y |  |  | cfg/i/manager/satReset/source | RemoteVoltageSignal |  |  |  |  | Must Configure 3pi Board
| VAV - SAT SP's | Not Developed | Heat SAT Low |  |  | Setpoint |  |  |  | sp/i/saTempHeatSP/min | [12 empty] | This is the desired Supply Air Temperature to be maintained during the heating mode of operation. When Supply Air Reset Source has been configured, the SAT Heating Setpoint is adjusted down to this value as the reset source temperature rises to the SAT Heating High Reset Source Setpoint.
|  | Not Developed | Heat SAT High |  |  | Setpoint |  |  |  | sp/i/saTempHeatSP/max | [12 empty] | When the Supply Air Reset Source has been configured, the SAT Heating Setpoint is adjusted up to this value as the reset source temperature falls to the SAT Heating Low Reset Source Setpoint.
|  | Not Developed | Source Heat SAT Low | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/heat/minValue | [12 empty] | As the reset source drops to this temperature, the supply air setpoint rises to what the ‘SAT High Reset Limit’ is set at.
|  | Not Developed | Source Heat SAT High | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/heat/maxValue | [8 empty] | F or C | 0 | 250 |  | As the reset source rises to this temperature, the supply air setpoint drops to what the ‘SAT Setpoint or Low SAT Limit for Reset’ is set at.
|  | Not Developed | Cool SAT Low |  |  | Setpoint |  |  |  | sp/i/saTempCoolSP/min | [8 empty] | F or C | 0 | 100 | 55 | This is the desired Supply Air Temperature to be maintained during the cooling mode of operation. When supply air reset has been configured, the SAT Cooling Setpoint is adjusted down to this value as the reset source temperature rises to the SAT Cooling High Reset Source Setpoint.
|  | Not Developed | Cool SAT High |  |  | Setpoint |  |  |  | sp/i/saTempCoolSP/max | [8 empty] | F or C | 0 | 100 | 65 | When the Supply Air Reset Source is configured, the SAT Cooling Setpoint is adjusted up to this value as the reset source temperature falls to the SAT Cooling Low Reset Source Setpoint.
|  | Not Developed | Source Cool SAT Low | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/cool/minValue | [8 empty] | F or C | -30 | 250 |  | As the reset source drops to this temperature, the supply air setpoint rises to what the ‘SAT High Reset Limit’ is set at.
|  | Not Developed | Source Cool SAT High | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/cool/maxValue | [8 empty] | F or C | -30 | 250 |  | As the reset source rises to this temperature, the supply air setpoint drops to what the ‘SAT Setpoint or Low SAT Limit for Reset’ is set at.
| VAV - DDC SP's | Not Developed | Min Voltage | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/minVolts
|  | Not Developed | Max Voltage | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/maxVolts
|  | Not Developed | Min Volt Cooling Temperature | Retained | working | Setpoint |  |  |  | sp/i/saTempCoolSP/min
|  | Not Developed | Max Volt Cooling Temperature | Retained | working | Setpoint |  |  |  | sp/i/saTempCoolSP/max
|  | Not Developed | Min Volt Heating Temp |  |  | Setpoint |  |  |  | sp/i/saTempHeatSP/min
|  | Not Developed | Max Volt Heating Temperature |  |  | Setpoint |  |  |  | sp/i/saTempHeatSP/max
OA Control | OA Setpoints | Not Developed | Occupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/occCoolSpaceTempSP | [8 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Not Developed | Occupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/occHeatSpaceTempSP | [8 empty] | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
| OA Control - SAT Reset | Not Developed | No SAT Reset |  |  | Radio Button | n |  |  | cfg/i/manager/satReset/enable | boolean
|  | Not Developed | Enable SAT Reset |  |  | Radio Button |  |  |  | cfg/i/manager/satReset/enable | boolean
|  | Not Developed | Outside Air |  |  | Radio Button |  |  |  | cfg/i/manager/satReset/source | OA
|  | Not Developed | Space Air |  |  | Radio Button |  |  |  | cfg/i/manager/satReset/source | Space
|  | Not Developed | Return Air Control |  |  | Radio Button |  |  |  | cfg/i/manager/satReset/source | Return
|  | Not Developed | Fan VFD |  |  | Radio Button |  |  |  | cfg/i/manager/satReset/source | SupplyFanSpeed
|  | Not Developed | Remote Voltage Signal |  |  | Radio Button |  |  |  | cfg/i/manager/satReset/source | RemoteVoltageSignal |  |  |  |  | Must Configure 3pi Board
| VAV - DDC SP's | Not Developed | Min Voltage | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/minVolts
|  | Not Developed | Max Voltage | Retained | working | Setpoint |  |  |  | cfg/i/manager/satReset/source/maxVolts
|  | Not Developed | Min Volt Cooling Temperature | Retained | working | Setpoint |  |  |  | sp/i/saTempCoolSP/min
|  | Not Developed | Max Volt Cooling Temperature | Retained | working | Setpoint |  |  |  | sp/i/saTempCoolSP/max
|  | Not Developed | Min Volt Heating Temp | Retained | working | Setpoint |  |  |  | sp/i/saTempHeatSP/min
|  | Not Developed | Max Volt Heating Temperature | Retained | working | Setpoint |  |  |  | sp/i/saTempHeatSP/max
OA + Return Air Control | OA + RA Setpoints | Not Developed | Unoccupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | [8 empty] | F or C | -30 | 110 | 68 | This is the Mode Enable Setpoint that calls for Occupied Heating Mode. When the HVAC mode enable source temperature is below this value will put the unit into heating mode.
|  | Not Developed | Unoccupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | [8 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
3rd Party Interface | 3pi Type | Can't Test | Thermostat |  |  | Radio Button | n
|  | Can't Test | Heat Pump Thermostat |  |  | Radio Button | y
|  | Can't Test | DDC |  |  | Radio Button | y
| Heat Pump Thermostat Type | Can't Test | Fail to Heat |  |  | Radio Button | n
|  | Can't Test | Fail to Cool |  |  | Radio Button | n
| DDC Control Enables | Can't Test | Heat Wheel |  |  | Checkbox | n
|  | Can't Test | Supply Fan |  |  | Checkbox | y
|  | Can't Test | Return/Exhaust Fan |  |  | Checkbox | y |  |  | This hasn't been defined yet
|  | Can't Test | OA/Econ Damper |  |  | Checkbox | y
|  | Can't Test | SAT Reset |  |  | Checkbox | y
| DDC Supply Fan Setpoints | Can't Test | Min Voltage |  |  | Setpoint
|  | Can't Test | Max Voltage |  |  | Setpoint
| DDC Return/Exhaust Fan Setpoints | Can't Test | Min Voltage |  |  | Setpoint
|  | Can't Test | Max Voltage |  |  | Setpoint
| DDC OA/Econ Damper Setpoints | Can't Test | Min Voltage |  |  | Setpoint
|  | Can't Test | Max Voltage |  |  | Setpoint
| VAV - DDC SP's | Can't Test | Min Voltage |  |  | Setpoint
|  | Can't Test | Max Voltage |  |  | Setpoint
|  | Can't Test | Min Volt Cooling Temperature |  |  | Setpoint
|  | Can't Test | Max Volt Cooling Temperature |  |  | Setpoint
|  | Can't Test | Min Volt Heating Temp |  |  | Setpoint
|  | Can't Test | Max Volt Heating Temperature |  |  | Setpoint
Return Air Control | Return Air Setpoints | Not Developed | Occupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/occCoolSpaceTempSP | [8 empty] | F or C
|  | Not Developed | Unoccupied Cooling Setpoint |  |  | Setpoint |  |  |  | sp/i/occHeatSpaceTempSP | [8 empty] | F or C
|  | Not Developed | Occupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccCoolSpaceTempSP | [8 empty] | F or C | -30 | 110 | 80 | This is the mode enable setpoints that calls for unoccupied cooling mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT cooling setpoint
|  | Not Developed | Unoccupied Heating Setpoint |  |  | Setpoint |  |  |  | sp/i/unoccHeatSpaceTempSP | [8 empty] | F or C | -30 | 110 | 60 | This is the mode enable setpoints that calls for unoccupied heating mode. If this value is ever exceeded while in unoccupied mode, it will turn the unit back on and control to our SAT heating setpoint
Unknown
Scalings | Temp Scaling | Dev and failed testing | Fahrenheit (Default) | Retained |  | Radio Button | n |  |  | cfg/i/displayInCelcius | false
|  | Dev and failed testing | Celcius | Retained |  | Radio Button | n |  |  | cfg/i/displayInCelcius | true
| Pressure Scaling | Can't Test | PSI |  |  | Radio Button | n
|  | Can't Test | "WG |  |  | Radio Button | n
| Airflow Scaling | Can't Test | CFM |  |  | Radio Button | n
|  | Can't Test | l/s |  |  | Radio Button | n
Unknown
Daylight Savings | Daylight Savings Enable | Can't Test | Daylight Savings Schedule Enable |  |  | checkbox | y
| Daylight Savings SP's | Can't Test | Start Date |  |  | Date Selector
|  | Can't Test | End Date |  |  | Date Selector
Unknown
Simultaneous Heat/Cool | Simultaneous Heat/Cool | Not Developed | Disabled | Topic retained | [5 empty] | cfg/i/manager/simulHeatCool
|  | Not Developed | Enabled | Topic retained | [5 empty] | cfg/i/manager/simulHeatCool
Apply Config | Apply Config | [6 empty] | cfg/i/gc/doConfig | true
sts/i/gc/configResult

## Unit Settings - Boards
[ | Page | State | Feature | Dev Changes | dev status | Type | Chevron? | Topic Notes | UI Topic | UI Payload | Topic | Payload |  | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Boards | Type | Can't Test | Unit Manager |  |  | Checkbox | y
|  | Dev and failed testing | Power-Comm Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/powerComm | boolean
|  | Dev and failed testing | Air Handler Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/ahu | boolean
|  | Dev and failed testing | Cooling Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/cooling | boolean
|  | Dev and failed testing | Heating Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/heating | boolean
|  | Dev and failed testing | Energy Recovery Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/energyRecovery | boolean
|  | Dev and failed testing | Preheat Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/preheat | boolean
|  | Dev and failed testing | Outside Air Board | 1)UI topic and payload with retain |  | Checkbox | y |  | ui/config/boardSelection/outsideAir | boolean
Can't Test
Unit Manager |  | Unknown
Can't Test
Unit Manager | Unit Manager - BACnet | Dev and passed testing | MS/TP |  |  | Radio Button | y |  |  |  | cfg/i/gc/bacnetConfig/protocol | mstp
|  | Dev and passed testing | IP |  |  | Radio Button | y |  |  |  | cfg/i/gc/bacnetConfig/protocol | ip
| BACnet MS/TP - Baud Rate | Dev and passed testing | 4800 |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 4800
|  | Dev and passed testing | 9600 |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 9600
|  | Dev and passed testing | 19200 |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 19200
|  | Dev and passed testing | 38400 |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 38400
|  | Dev and passed testing | 57600 |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 57600
|  | Dev and passed testing | 115200 |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/baudRate | 115200
| BACnet MS/TP - MAC Address | Dev and passed testing | MAC Address |  |  | Setpoint | n |  |  |  | cfg/i/gc/bacnetConfig/mstp/macAddress | {{int}}
| BACnet MS/TP - Device ID | Dev and passed testing | Device ID |  |  | Setpoint | n |  |  |  | cfg/i/gc/bacnetConfig/deviceID | {{int}}
| BACnet IP - Device ID | Dev and passed testing | Device ID |  |  | Setpoint | n |  |  |  | cfg/i/gc/bacnetConfig/deviceID | {{int}}
| BACnet IP - BBMD - Foreign Device Enabled | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/enable | false
|  | Not Developed | Enabled |  |  | Radio Button | y |  |  |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/enable | true
| BACnet IP - BBMD - Network | Not Developed | BBMD IPv4 Address |  |  | Setpoint |  |  |  |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/BBMDIP | 192.168.100.100
|  | Not Developed | Network Port |  |  | Setpoint |  |  |  |  | cfg/i/gc/bacnetConfig/ip/foreignDevice/BBMDPort | {{int}}
| Unit Manager - Network | Not Developed | DHCP - Auto |  |  | Toggle |  | Stratus/IP is only for status |  |  | Stratus/IP | { "dhcp": true, "dns": [ "10.60.0.95", "10.60.0.96" ], "gateway": "10.60.100.1", "ip": "10.60.100.76", "mac": "6C:DF:FB:60:89:68", "netmask": 23 } |  | Stratus/IPConfigChange | { "dhcp": false, "dns": [ ], "gateway": "192.168.1.1", "ip": "192.168.1.102", "netmask": 24 }
|  | Not Developed | DHCP - Static |  |  | Toggle |  |  |  |  | Stratus/IP |  |  | Stratus/IPConfigChange
|  | Not Developed | IPv4 |  |  | Setpoint |  |  |  |  | Stratus/IP |  |  | Stratus/IPConfigChange
|  | Not Developed | Netmask |  |  | Setpoint |  |  |  |  | Stratus/IP |  |  | Stratus/IPConfigChange
|  | Not Developed | Gateway Address |  |  | Setpoint |  |  |  |  | Stratus/IP |  |  | Stratus/IPConfigChange
|  | Not Developed | DNS Server Address (optional) |  |  | Setpoint |  |  |  |  | Stratus/IP |  |  | Stratus/IPConfigChange
|  | Not Developed | MAC Address |  |  | Status |  |  |  |  | Stratus/IP |  |  | Stratus/IPConfigChange
|  | Not Developed | Ethernet |  |  | Status |  |  |  |  | Stratus/IP
| Unit Manager - EBUS | Not Developed | Low Speed |  |  | Radio Button | n
|  | Not Developed | High Speed |  |  | Radio Button | n
Can't Test
Preheat Board |  | Unknown
Can't Test
Preheat Board | Count | Not Developed | 1 Board |  |  | Radio Button | n |  |  |  | cfg/i/gc/boardCount/preheat | 1
|  | Not Developed | 2 Boards |  |  | Radio Button | n |  |  |  | cfg/i/gc/boardCount/preheat | 2
Board 1 | Preheat Board 1 | Not Developed | Unique ID |  |  | Radio Button or Status | s |  |  |  | cfg/i/gc/boards/preheat/1/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
Board 1 Temps | Temp 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/1/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/1/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/1/selection | preheatLeavingAirTemp
| Temp 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/2/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/2/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/2/selection | preheatLeavingAirTemp
| Temp 3 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/3/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/3/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/3/selection | preheatLeavingAirTemp
| Temp 4 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/4/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/4/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/4/selection | preheatLeavingAirTemp
| Temp 5 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/5/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/5/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/5/selection | preheatLeavingAirTemp
| Temp 6 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/6/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/6/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/6/selection | preheatLeavingAirTemp
| Temp 7 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/7/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/7/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/7/selection | preheatLeavingAirTemp
| Temp 8 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/8/selection | none
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/8/selection | preheatEnteringAirTemp
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/THERM/8/selection | preheatLeavingAirTemp
Board 1 Mouts | Mout 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/1/MOUT/8/selection | BACnetPassthrough
Not Developed
Board 2 | Preheat Board 2 | Not Developed | Unique ID |  |  | Radio Button or Status | n |  |  |  | cfg/i/gc/boards/preheat/2/uuid |  |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
Board 2 Temps | Temp 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/1/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/1/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/1/selection
| Temp 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/2/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/2/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/2/selection
| Temp 3 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/3/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/3/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/3/selection
| Temp 4 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/4/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/4/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/4/selection
| Temp 5 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/5/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/5/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/5/selection
| Temp 6 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/6/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/6/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/6/selection
| Temp 7 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/7/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/7/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/7/selection
| Temp 8 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/8/selection
|  | Not Developed | Entering Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/8/selection
|  | Not Developed | Leaving Air |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/THERM/8/selection
Board 2 Mouts | Mout 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | none
|  | Not Developed | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | heatEnable
|  | Not Developed | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/preheat/2/MOUT/8/selection | BACnetPassthrough
Can't Test
Can't Test
Outside Air Board |  | Unknown
Can't Test
Outside Air Board | Count | Dev and passed testing | 1 Board |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/outsideAir | 1
|  | Dev and passed testing | 2 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/outsideAir | 2
| Board 1 | Dev and passed testing | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/outsideAir/1/uuid |  |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Dampers | Dev and passed testing | Damper 1 |  |  | Checkbox | y | This is a weird way of doing this, these will technically set the 'selection' of the damper to none when unchecked, but don't do anything when they are checked. Everywhere else we've had a radio option for 'none' rather than doing it this way |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | none
|  | Dev and passed testing | Damper 2 |  |  | Checkbox | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | none
|  | Dev and passed testing | Damper 3 |  |  | Checkbox | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | none
| Damper 1 Type | Dev and passed testing | Outside Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | oaDamper
|  | Dev and passed testing | Return Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | motorizedExhaustDamper
|  | Dev and passed testing | Energy Recovery Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/selection | erSupplyDamper
| Outside Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n | End switch is linked to the damper connector's location, not what type it is |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Return Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/1/endSwitch | true
| Damper 2 Type | Dev and passed testing | Outside Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | oaDamper
|  | Dev and passed testing | Return Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | motorizedExhaustDamper
|  | Dev and passed testing | Energy Recovery Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/selection | erSupplyDamper
| Outside Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Return Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/2/endSwitch | true
| Damper 3 Type | Dev and passed testing | Outside Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | oaDamper
|  | Dev and passed testing | Return Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | motorizedExhaustDamper
|  | Dev and passed testing | Energy Recovery Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/selection | erSupplyDamper
| Outside Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Return Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/DAMPER/3/endSwitch | true
| Binary Input 1 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/1/selection | dirtyPreFilterSwitch
| Binary Input 2 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/2/selection | dirtyPreFilterSwitch
| Binary Input 3 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/3/selection | dirtyPreFilterSwitch
| Binary Input 4 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/1/BIN/4/selection | dirtyPreFilterSwitch
| Thermistor Analog Inputs | Dev and passed testing | Outside Air Temp Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/1/THERM/1/selection | boolean
|  | Dev and passed testing | Return Air Temp Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/1/THERM/2/selection | boolean
|  | Dev and passed testing | Building Pressure Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/1/THERM/3/selection | boolean
|  | Dev and passed testing | Exhaust Duct Static Pressure Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/1/THERM/4/selection | boolean
| Board 2 | Dev and passed testing | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/outsideAir/2/uuid |  |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Dampers | Dev and passed testing | Damper 1 |  |  | Checkbox | y | This is a weird way of doing this, these will technically set the 'selection' of the damper to none when unchecked, but don't do anything when they are checked. Everywhere else we've had a radio option for 'none' rather than doing it this way |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | none
|  | Dev and passed testing | Damper 2 |  |  | Checkbox | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | none
|  | Dev and passed testing | Damper 3 |  |  | Checkbox | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection | none
| Damper 1 Type | Dev and passed testing | Outside Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | oaDamper
|  | Dev and passed testing | Return Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | motorizedExhaustDamper
|  | Dev and passed testing | Energy Recovery Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/selection | erSupplyDamper
| Outside Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n | End switch is linked to the damper connector's location, not what type it is |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Return Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/1/endSwitch | true
| Damper 2 Type | Dev and passed testing | Outside Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | oaDamper
|  | Dev and passed testing | Return Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | motorizedExhaustDamper
|  | Dev and passed testing | Energy Recovery Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/selection | erSupplyDamper
| Outside Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Return Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Exhaust Air End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Energy Recovery Bypass End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/2/endSwitch | true
| Damper 3 Type | Dev and passed testing | Outside Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Dev and passed testing | Return Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Dev and passed testing | Return Air Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Dev and passed testing | Exhaust Air |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
|  | Dev and passed testing | Energy Recovery Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/selection
| Outside Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Return Air End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Exhaust Air End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Energy Recovery Bypass End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/DAMPER/3/endSwitch
| Binary Input 1 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/1/selection | dirtyPreFilterSwitch
| Binary Input 2 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/2/selection | dirtyPreFilterSwitch
| Binary Input 3 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/3/selection | dirtyPreFilterSwitch
| Binary Input 4 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | none
|  | Dev and passed testing | Supply Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | exhaustAirflowSwitch
|  | Dev and passed testing | Dirty Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | dirtyFilterSwitch
|  | Dev and passed testing | Dirty Pre-Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/outsideAir/2/BIN/4/selection | dirtyPreFilterSwitch
| Thermistor Analog Inputs | Dev and passed testing | Outside Air Temp Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/2/THERM/1/selection | boolean
|  | Dev and passed testing | Return Air Temp Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/2/THERM/2/selection | boolean
|  | Dev and passed testing | Building Pressure Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/2/THERM/3/selection | boolean
|  | Dev and passed testing | Exhaust Duct Static Pressure Enable |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/outsideAir/2/THERM/4/selection | boolean
Can't Test
Heating Board |  | Unknown
Can't Test
Heating Board | Count | Dev and passed testing | 1 Board |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/heating | 1
|  | Dev and passed testing | 2 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/heating | 2
| Board 1 | Dev and passed testing | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/heating/1/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/1/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/1/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/2/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/2/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/2/selection | BACnetPassthrough
| Binary Input 3 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/3/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/3/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/3/selection | BACnetPassthrough
| Binary Input 4 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/4/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/4/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/4/selection | BACnetPassthrough
| Binary Input 5 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/5/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/5/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/BIN/5/selection | BACnetPassthrough
| Mout 1 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | none | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | inducerFanLowSpeed | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | none | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | heatEnable | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/7/selection | BACnetPassthrough | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
| Mout 8 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/8/selection | BACnetPassthrough
| Mod Gas Valve 1 | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/ModGasValve/1/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/ModGasValve/1/selection | modGasValve
| Mod Gas Valve 2 | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/ModGasValve/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/ModGasValve/2/selection | modGasValve
| Board 2 | Dev and passed testing | Unique ID |  |  | Status |  |  |  |  | cfg/i/gc/boards/heating/2/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/1/selection | none | [13 empty] | IF Valve is configred as "Enabled" please gray out and default to "ignition proof", if it is made "disabled" default to "not used" and degray the box
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/1/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/2/selection | none | [13 empty] | IF Valve is configred as "Enabled" please gray out and default to "ignition proof", if it is made "disabled" default to "not used" and degray the box
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/2/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/2/selection | BACnetPassthrough
| Binary Input 3 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/3/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/3/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/3/selection | BACnetPassthrough
| Binary Input 4 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/4/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/4/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/4/selection | BACnetPassthrough
| Binary Input 5 - Gas Ignition Feedback | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/5/selection | none
|  | Dev and passed testing | Ignition Proof |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/5/selection | ignitionProof
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/BIN/5/selection | BACnetPassthrough
| Mout 1 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | inducerFanLowSpeed | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | heatEnable | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | none | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | heatEnable | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/6/selection | BACnetPassthrough | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
| Mout 7 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | scrSignal
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Dev and passed testing | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | none
|  | Dev and passed testing | SCR Signal |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | scrSignal | [13 empty] | SCR Signal can only be chosen 1 time. So once it is chosen, gray out SCR signal for every other Mout.
|  | Dev and passed testing | Heat Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Inducer Fan Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | inducerFanLowSpeed
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/MOUT/8/selection | BACnetPassthrough
| Mod Gas Valve 1 | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/ModGasValve/1/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/ModGasValve/1/selection | modGasValve | [10 empty] | x
| Mod Gas Valve 2 | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/ModGasValve/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/2/ModGasValve/2/selection | modGasValve | [10 empty] | x
Can't Test
Energy Recovery Board |  | Unknown
Can't Test
Energy Recovery Board | Count | Not Developed | 1 Board |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/heatWheel | 1
|  | Not Developed | 2 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/heatWheel | 2
| Board 1 | Not Developed | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/heatWheel/1/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Thermistor 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/1/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/1/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/1/selection | erExhaustLeavingAirTemp
| Thermistor 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 3 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 4 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/3/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/3/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/3/selection | erExhaustLeavingAirTemp
| Thermistor 5 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/4/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/4/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/4/selection | erExhaustLeavingAirTemp
| Thermistor 6 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/5/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/5/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/THERM/5/selection | erExhaustLeavingAirTemp
| Binary Input 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | none
|  | Not Developed | Intake Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | rotationStatus
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | none
|  | Not Developed | Intake Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | rotationStatus
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/1/BIN/2/selection | BACnetPassthrough
| Bypass 1 | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | none
|  | Not Developed | Supply Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | erSupplyDamper
|  | Not Developed | Exhaust Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | erExhaustDamper
|  | Not Developed | Single Supply/Exhaust Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/selection | erSingleSupplyExhaustDamper
| Bypass 2 | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | none
|  | Not Developed | Supply Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | erSupplyDamper
|  | Not Developed | Exhaust Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | erExhaustDamper
|  | Not Developed | Single Supply/Exhaust Bypass |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/selection | erSingleSupplyExhaustDamper
| Bypass 1 End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/1/endSwitch | true
| Bypass 2 End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/DAMPER/2/endSwitch | true
| VFD | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | none
|  | Not Developed | Enabled |  |  | Radio Button | y | needs chevron to VFD flow |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | heatWheel
| VFD | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | none
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/selection | heatWheel
| Heat Wheel Overload Input | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/overloadInput | none
|  | Not Developed | Overload Input 1 |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/overloadInput | overload1
|  | Not Developed | Overload Input 2 |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/overloadInput | overload2
| Supply Fan Type | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/vfdPortType | none
|  | Not Developed | Communicating |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/vfdPortType | commFan
|  | Not Developed | 0-10 |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Not Developed | Min Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/analogMinVolts | {{float}}
|  | Not Developed | Max Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/analogMaxVolts | {{float}}
| Motor Type | Not Developed | Electromagnet Motor (EM) |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/isPMM | false
|  | Not Developed | Permanent Magnet Motor (PMM) |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/isPMM | true
| Electromagnet Motor Rating | Not Developed | Motor HP |  |  | Setpoint |  | This data is tied to the VFD port, make sure the PinLocation is in the topic correctly for all motor data entries |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/HP
|  | Not Developed | Motor RPM |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/RPM
|  | Not Developed | Service Factor |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/serviceFactor
|  | Not Developed | Motor FLA |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/FLA
|  | Not Developed | Drive Min Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Not Developed | Motor HP |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/HP
|  | Not Developed | Motor RPM |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/RPM
|  | Not Developed | Service Factor |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/serviceFactor
|  | Not Developed | Motor FLA |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/FLA
|  | Not Developed | Drive Min Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/nameplateFreq
|  | Not Developed | Ld |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.Ld
|  | Not Developed | Lq |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.Lq
|  | Not Developed | BEMF |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.BEMF
|  | Not Developed | Rs |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/pmm.Rs
| Voltage | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 0
|  | Not Developed | 208 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 208
|  | Not Developed | 230 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 230
|  | Not Developed | 460 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 460
|  | Not Developed | 575 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/VFD/1/motorData/motorVoltage | 575
| Mout 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | none
|  | Not Developed | Heat Wheel Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | heatWheelEnable
|  | Not Developed | Heat Wheel Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | heatWheelLowSpeed
|  | Not Developed | Bypass Damper Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | bypassDamperEnable
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/1/MOUT/1/selection | BACnetPassthrough
| Board 2 | Not Developed | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/heatWheel/2/uuid | {{int}}
| Thermistor 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/1/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/1/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/1/selection | erExhaustLeavingAirTemp
| Thermistor 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 3 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/2/selection | erExhaustLeavingAirTemp
| Thermistor 4 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/3/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/3/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/3/selection | erExhaustLeavingAirTemp
| Thermistor 5 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/4/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/4/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/4/selection | erExhaustLeavingAirTemp
| Thermistor 6 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/5/selection | none
|  | Not Developed | Intake Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/5/selection | erIntakeLeavingAirTemp
|  | Not Developed | Exhaust Leaving Air Temp |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/THERM/5/selection | erExhaustLeavingAirTemp
| Binary Input 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | none
|  | Not Developed | Intake Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | rotationStatus
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | none
|  | Not Developed | Intake Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | intakeFilterSwitch
|  | Not Developed | Exhaust Filter Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | exhaustFilterSwitch
|  | Not Developed | Rotation Status |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | rotationStatus
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatwheel/2/BIN/2/selection | BACnetPassthrough
| Bypass 1 | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/selection | none
|  | Not Developed | Enabled |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/selection | erSupplyDamper
| Bypass 2 | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/selection | none
|  | Not Developed | Enabled |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/selection | erReturnDamper
| Bypass 1 End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/1/endSwitch | true
| Bypass 2 End Switch | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/endSwitch | false
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/DAMPER/2/endSwitch | true
| VFD | Not Developed | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/1/selection | none
|  | Not Developed | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/1/selection | heatWheel
| Heat Wheel Overload Input | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/overloadInput | none
|  | Not Developed | Overload Input 1 |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/overloadInput | overload1
|  | Not Developed | Overload Input 2 |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/overloadInput | overload2
| Supply Fan Type | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/vfdPortType | none
|  | Not Developed | Communicating |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/vfdPortType | commFan
|  | Not Developed | 0-10 |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Not Developed | Min Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/analogMinVolts | {{float}}
|  | Not Developed | Max Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/analogMaxVolts | {{float}}
| Motor Type | Not Developed | Electromagnet Motor (EM) |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/isPMM | false
|  | Not Developed | Permanent Magnet Motor (PMM) |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/isPMM | true
| Electromagnet Motor Rating | Not Developed | Motor HP |  |  | Setpoint |  | This data is tied to the VFD port, make sure the PinLocation is in the topic correctly for all motor data entries |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/HP
|  | Not Developed | Motor RPM |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/RPM
|  | Not Developed | Service Factor |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/serviceFactor
|  | Not Developed | Motor FLA |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/FLA
|  | Not Developed | Drive Min Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Not Developed | Motor HP |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/HP
|  | Not Developed | Motor RPM |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/RPM
|  | Not Developed | Service Factor |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/serviceFactor
|  | Not Developed | Motor FLA |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/FLA
|  | Not Developed | Drive Min Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMinFreq
|  | Not Developed | Drive Max Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/driveMaxFreq
|  | Not Developed | Nameplate Frequency |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/nameplateFreq
|  | Not Developed | Ld |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.Ld
|  | Not Developed | Lq |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.Lq
|  | Not Developed | BEMF |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.BEMF
|  | Not Developed | Rs |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/pmm.Rs
| Voltage | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 0
|  | Not Developed | 208 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 208
|  | Not Developed | 230 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 230
|  | Not Developed | 460 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 460
|  | Not Developed | 575 vac | Topic changed to field value retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/VFD/2/motorData/motorVoltage | 575
| Mout 1 | Not Developed | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | none
|  | Not Developed | Heat Wheel Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | heatWheelEnable
|  | Not Developed | Heat Wheel Low Speed |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | heatWheelLowSpeed
|  | Not Developed | Bypass Damper Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | bypassDamperEnable
|  | Not Developed | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heatWheel/2/MOUT/2/selection | BACnetPassthrough
Can't Test
Can't Test
Power-Comm Board |  | Unknown
Can't Test
Power-Comm Board | Count | Dev and failed testing | 1 Board |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/powerComm | 1
|  | Dev and failed testing | 2 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/powerComm | 2
|  | Dev and failed testing | 3 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/powerComm | 3
|  | Dev and failed testing | 4 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/powerComm | 4
|  | Dev and failed testing | 5 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/powerComm | 5
|  | Dev and failed testing | 6 Boards |  |  | Radio Button | y |  |  |  | cfg/i/gc/boardCount/powerComm | 6
| Board 1 | Dev and passed testing | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/powerComm/1/uuid | {{string}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/BIN/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/BIN/3/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/1/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | none |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/1/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/1/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/1/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/hasPressure | boolean | [13 empty] | Ourside EXV2 does not publish
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/1/sporlan/exv2/hasTemperature | boolean
| Comm 2 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/2/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | none |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/2/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/2/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/2/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/hasPressure | boolean
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/2/sporlan/exv2/hasTemperature | boolean
| Comm 3 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/3/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | none |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/3/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/3/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/3/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/hasPressure | boolean
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/3/sporlan/exv2/hasTemperature | boolean
| Comm 4 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/4/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | none |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/4/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/4/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/4/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/hasPressure | boolean
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/4/sporlan/exv2/hasTemperature | boolean
| Comm 5 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/5/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | none |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/5/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/5/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/5/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/6/type | none | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | none |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/6/type | sporlan | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/1/EXVComm/6/type | sporlanVI | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/1/EXVComm/6/type | sanhua | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/1/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 2 | Dev and passed testing | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/powerComm/2/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/BIN/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/BIN/3/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/1/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/1/sporlan/type | none |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/1/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/1/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/1/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/1/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/1/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/1/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/2/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | none |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/2/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/2/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/2/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/3/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | none |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/3/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/3/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/3/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/4/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | none |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/4/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/4/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/4/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/5/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | none |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/5/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/5/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/5/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/6/type | none | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | none |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/6/type | sporlan | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/2/EXVComm/6/type | sporlanVI | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/2/EXVComm/6/type | sanhua | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/2/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 3 | Dev and passed testing | Unique ID |  |  | Radio Button or Status |  |  |  |  | cfg/i/gc/boards/powerComm/3/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/BIN/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/BIN/3/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/1/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/type | none |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/1/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/1/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/1/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/1/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/2/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/type | none |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/2/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/2/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/2/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/3/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | none |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/3/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/3/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/3/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/4/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | none |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/4/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/4/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/4/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/5/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | none |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/5/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/5/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/5/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/6/type | none | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | none |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/6/type | sporlan | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/3/EXVComm/6/type | sporlanVI | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/3/EXVComm/6/type | sanhua | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/3/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 4 | Dev and passed testing | Unique ID |  |  | Radio Button or Status | n |  |  |  | cfg/i/gc/boards/powerComm/4/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/BIN/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/BIN/3/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/1/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/type | none |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/1/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/1/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/1/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/1/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/2/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/type | none |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/2/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/2/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/2/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/3/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | none |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/3/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/3/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/3/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/4/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | none |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/4/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/4/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/4/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/5/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | none |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/5/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/5/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/5/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/6/type | none | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | none |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/6/type | sporlan | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/4/EXVComm/6/type | sporlanVI | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/4/EXVComm/6/type | sanhua | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/4/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 5 | Dev and passed testing | Unique ID |  |  | Radio Button or Status | n |  |  |  | cfg/i/gc/boards/powerComm/5/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/BIN/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/BIN/3/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/1/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/type | none |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/1/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/1/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/1/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/1/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/2/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/type | none |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/2/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/2/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/2/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/3/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | none |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/3/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/3/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/3/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/4/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | none |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/4/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/4/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/4/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/5/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | none |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/5/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/5/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/5/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/6/type | none | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | none |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/6/type | sporlan | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/5/EXVComm/6/type | sporlanVI | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/5/EXVComm/6/type | sanhua | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/5/EXVComm/6/sporlan/exv2/hasTemperature | true
| Board 6 | Dev and passed testing | Unique ID |  |  | Radio Button or Status | n |  |  |  | cfg/i/gc/boards/powerComm/6/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Binary Input 1 - 24V Power Alert | Dev and passed testing | Disabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/BIN/1/selection | none
|  | Dev and passed testing | Enabled | Topic-reatined |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/BIN/1/selection | 24VPowerAlert
| Binary Input 1 - PBO Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/BIN/2/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/BIN/2/selection | PBOAlert
| Binary Input 1 - Power Supply Thermal Alert | Dev and passed testing | Disabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/BIN/3/selection | none
|  | Dev and passed testing | Enabled |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/BIN/3/selection | powerSupplyThermalAlert
| Comm 1 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/1/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/type | none |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/1/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/1/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/1/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sanhua
| Comm 1 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv1/location | outdoor
| Comm 1 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv2/location | outdoor
| Comm 1 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/1/sporlan/exv2/hasTemperature | true
| Comm 2 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/2/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/type | none |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/2/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/2/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/2/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sanhua
| Comm 2 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv1/location | outdoor
| Comm 2 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv2/location | outdoor
| Comm 2 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/2/sporlan/exv2/hasTemperature | true
| Comm 3 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/3/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | none |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/3/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/3/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/3/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/selection | sanhua
| Comm 3 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv1/location | outdoor
| Comm 3 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/location | outdoor
| Comm 3 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor |  |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/3/sporlan/exv2/hasTemperature | true
| Comm 4 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/4/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | none |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/4/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/4/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/4/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/selection | sanhua
| Comm 4 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv1/location | outdoor
| Comm 4 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/location | outdoor
| Comm 4 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/4/sporlan/exv2/hasTemperature | true
| Comm 5 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/5/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | none |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/5/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/5/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/5/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/selection | sanhua
| Comm 5 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv1/location | outdoor
| Comm 5 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/location | outdoor
| Comm 5 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/5/sporlan/exv2/hasTemperature | true
| Comm 6 | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/6/type | none | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | none |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | none
|  | Dev and failed testing | Sporlan | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/6/type | sporlan | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlan |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlan
|  | Dev and failed testing | Sporlan Vapor Injection | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | y |  | ui/cfg/boards/powerComm/6/EXVComm/6/type | sporlanVI | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sporlanVI |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sporlanVI
|  | Dev and failed testing | Sanhua | 1)Payload - field value 2)topics - field value 3)topic 2 & UI topic are retained |  | Radio Button | n |  | ui/cfg/boards/powerComm/6/EXVComm/6/type | sanhua | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/type | sanhua |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/selection | sanhua
| Comm 6 - Sporlan - EXV 1 | Dev and passed testing | Indoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv1/location | outdoor
| Comm 6 - Sporlan - EXV 2 | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | none
|  | Dev and passed testing | Indoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | indoor
|  | Dev and passed testing | Outdoor |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/location | outdoor
| Comm 6 - Sporlan - EXV 2 - Sensors | Dev and failed testing | Pressure Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasPressure | true
|  | Dev and failed testing | Temperature Sensor | Topic-reatined |  | Child Checkbox | n |  |  |  | cfg/i/gc/boards/powerComm/6/EXVComm/6/sporlan/exv2/hasTemperature | true
Can't Test
Cooling Board |  | Unknown
Can't Test
Cooling Board | Count | Dev and failed testing | 1 Board | [7 empty] | cfg/i/gc/boardCount/cooling | 1
|  | Dev and failed testing | 2 Boards | [7 empty] | cfg/i/gc/boardCount/cooling | 2
|  | Dev and failed testing | 3 Boards | [7 empty] | cfg/i/gc/boardCount/cooling | 3
|  | Dev and failed testing | 4 Boards | [7 empty] | cfg/i/gc/boardCount/cooling | 4
| Board 1 | Dev and passed testing | Unique ID |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | n | I don't need these, so UI only if you do need them | ui/cfg/boards/cooling/1/VFD/1/compressorSetup | none | cfg/i/gc/boards/cooling/1/VFD/1/selection | none
|  | Dev and failed testing | Single Compressor | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/1/VFD/1/compressorSetup | single | cfg/i/gc/boards/cooling/1/VFD/1/selection | compressor
|  | Dev and failed testing | Tandem | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/1/VFD/1/compressorSetup | tandem | cfg/i/gc/boards/cooling/1/VFD/1/selection | compressor
| Compressor 1 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/make | none
|  | Unknown | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/make | danfoss
|  | Unknown | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n | For now make a list of these to select from and publish it in the topic. |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH | topic changed to filed value and added retain |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/tonnage |  | Retained
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/make | none
|  | Not Tested | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/make | danfoss
|  | Not Tested | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None | topic changed to field valueand Retain added |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH | topic changed to field valueand Retain added |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH | topic changed to field valueand Retain added |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and failed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/tonnage
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/A2L/1/selection | none
|  | Not Tested | Cabinet |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/A2L/1/selection | cabinet
|  | Not Tested | Air Stream |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/A2L/1/selection | airstream
| Mout 1 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n | Unused for now
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Harness 2 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Analog Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/1/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | 2800 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | 3500 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/1/ReheatValve/1/stepCount | 6386 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom |  |  | Radio Button | n | [5 empty] | Retained | [12 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out
| Board 2 | Dev and passed testing | Unique ID |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | n | I don't need these, so UI only if you do need them | ui/cfg/boards/cooling/2/VFD/1/compressorSetup | none | cfg/i/gc/boards/cooling/2/VFD/1/selection | none
|  | Dev and failed testing | Single Compressor | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/2/VFD/1/compressorSetup | single | cfg/i/gc/boards/cooling/2/VFD/1/selection | compressor
|  | Dev and failed testing | Tandem | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/2/VFD/1/compressorSetup | tandem | cfg/i/gc/boards/cooling/2/VFD/1/selection | compressor
| Compressor 1 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/make | none
|  | Not Tested | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/make | danfoss
|  | Not Tested | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/tonnage
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 208 | Retained
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/make | none
|  | Not Tested | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/make | danfoss
|  | Not Tested | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/tonnage |  | Retained
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/A2L/1/selection | none
|  | Not Tested | Cabinet |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/A2L/1/selection | cabinet
|  | Not Tested | Air Stream |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/A2L/1/selection | airstream
| Mout 1 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n | Unused for now
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Harness 2 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Analog Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/2/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/ReheatValve/1/stepCount | 2800 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/ReheatValve/1/stepCount | 3500 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/2/ReheatValve/1/stepCount | 6386 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom |  |  | Radio Button | n | [5 empty] | Retained | [12 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out
| Board 3 | Dev and passed testing | Unique ID |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | n | I don't need these, so UI only if you do need them | ui/cfg/boards/cooling/3/VFD/1/compressorSetup | none | cfg/i/gc/boards/cooling/3/VFD/1/selection | none
|  | Dev and failed testing | Single Compressor | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/3/VFD/1/compressorSetup | single | cfg/i/gc/boards/cooling/3/VFD/1/selection | compressor
|  | Dev and failed testing | Tandem | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/3/VFD/1/compressorSetup | tandem | cfg/i/gc/boards/cooling/3/VFD/1/selection | compressor
| Compressor 1 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/make | none
|  | Unknown | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/make | danfoss
|  | Unknown | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/tonnage
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/make | none
|  | Not Tested | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/make | danfoss
|  | Not Tested | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/tonnage
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/A2L/1/selection | none
|  | Not Tested | Cabinet |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/A2L/1/selection | cabinet
|  | Not Tested | Air Stream |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/A2L/1/selection | airstream
| Mout 1 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n | Unused for now
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Harness 2 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Analog Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | supplyAirflowSwitch
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/3/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/ReheatValve/1/stepCount | 2800 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/ReheatValve/1/stepCount | 3500 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/3/ReheatValve/1/stepCount | 6386 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom |  |  | Radio Button | n | [5 empty] | Retained | [12 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out
| Board 4 | Dev and passed testing | Unique ID |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/uuid | {{int}} |  | Stratus/boardList | [ { "type": "cooling", "sn": "XYZ-34135", "ip": "192.168.100.70" }, { "type": "heating", "sn": "XYZ-34132", "ip": "192.168.100.110" }, { "type": "energyRec", "sn": "XYZ-34131", "ip": "192.168.100.120" }, { "type": "preheat", "sn": "XYZ-34133", "ip": "192.168.100.80" }, { "type": "airHandler", "sn": "XYZ-34134", "ip": "192.168.100.50" }, { "type": "outsideAir", "sn": "XYZ-34136", "ip": "192.168.100.60" }, { "type": "powerComm", "sn": "XYZ-34137", "ip": "192.168.100.10" } ]
| Refrigeration 1 - Compressor Setup | Dev and failed testing | None | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | n | I don't need these, so UI only if you do need them | ui/cfg/boards/cooling/4/VFD/1/compressorSetup | none | cfg/i/gc/boards/cooling/4/VFD/1/selection | none
|  | Dev and failed testing | Single Compressor | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/4/VFD/1/compressorSetup | single | cfg/i/gc/boards/cooling/4/VFD/1/selection | compressor
|  | Dev and failed testing | Tandem | 1)Payload - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/boards/cooling/4/VFD/1/compressorSetup | tandem | cfg/i/gc/boards/cooling/4/VFD/1/selection | compressor
| Compressor 1 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/type | 2Step
| Compressor 1 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/make | none
|  | Unknown | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/make | danfoss
|  | Unknown | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/runAsAnalog | true
| Compressor 1 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 1 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/model | YAW1601E-7X9-ECH
| Compressor 1 Voltages | Dev and passed testing | Min Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/minAnalogVolts
|  | Dev and passed testing | Max Voltage | Retained |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/maxAnalogVolts
| Compressor 1 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/tonnage |  | Retained
| Compressor 1 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/compressorData/voltage | 575
| Compressor 2 Type | Dev and passed testing | Digital | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | digital
|  | Dev and passed testing | VFD | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | vfd
|  | Dev and passed testing | On/Off | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | onOff
|  | Dev and passed testing | 2-Step | 1)topics - field value 2)UI topic is retained |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/type | 2Step
| Compressor 2 Make | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/make | none
|  | Unknown | Danfoss |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/make | danfoss
|  | Unknown | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/runAsAnalog | true
|  | Dev and passed testing | Copelan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/make | copeland
|  | Dev and failed testing | 0-10V |  |  | Child Checkbox | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/runAsAnalog | true
| Compressor 2 Model(s) (Danfoss) | Not Developed | None | [7 empty] | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | none | [13 empty] | NO DANFOSS MODELS AT THE MOMENT
| Compressor 2 Model(s) (Copelan) | Not Developed | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | none | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-5X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0471E-5X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH | topic changed to filed value and added retain
|  | Not Developed | YAW0471E-2X9-ASH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0471E-2X9-ASH
|  | Not Developed | YAW0661E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0661E-5X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0661E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0661E-7X9-ECH
|  | Not Developed | YAW0961E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0961E-5X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW0961E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW0961E-7X9-ECH
|  | Not Developed | YAW1341E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1341E-5X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1341E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1341E-7X9-ECH
|  | Not Developed | YAW1601E-5X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1601E-5X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
|  | Not Developed | YAW1601E-7X9-ECH |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/model | YAW1601E-7X9-ECH
| Compressor 2 Voltages | Dev and passed testing | Min Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/minAnalogVolts
|  | Dev and passed testing | Max Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/maxAnalogVolts
| Compressor 2 Tonnage | Dev and passed testing | Tonnage |  |  | Setpoint |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/tonnage |  | Retained
| Compressor 2 Voltages | Dev and passed testing | 208 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 208
|  | Dev and passed testing | 230 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 230
|  | Dev and passed testing | 460 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 460
|  | Dev and passed testing | 575 vac | Topic changed to field value retain added |  | Radio Button |  |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/tandemCompressor/voltage | 575
| A2L Port | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/A2L/1/selection | none
|  | Not Tested | Cabinet |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/A2L/1/selection | cabinet
|  | Not Tested | Air Stream |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/A2L/1/selection | airstream
| Mout 1 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | none
|  | Dev and passed testing | Unloader |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | unloader
|  | Dev and passed testing | Compressor Enable (Step) |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | compressorEnable(step)
|  | Dev and passed testing | Startup Solenoid |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | startupSolenoid
|  | Dev and passed testing | Reversing Valve |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | reversingValve
|  | Dev and passed testing | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/MOUT/2/selection | BACnetPassthrough
| Harness 1 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n | Unused for now
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Harness 2 | Not Tested | Not used |  |  | Radio Button | n
|  | Not Tested | Superheat |  |  | Radio Button | n
|  | Not Tested | Subcooling |  |  | Radio Button | n
| Analog Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/1/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/1/selection | BACnetPassthrough
| Analog Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/2/selection | none
|  | Not Tested | Analog Oil Level Sensor |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/AIN/2/selection | BACnetPassthrough
| Binary Input 1 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Not Tested | Not Used |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | none
|  | Not Tested | SUPPLY Airflow Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection
|  | Not Tested | Defrost Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | defrostSwitch
|  | Not Tested | Oil Level Switch |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | oilLevelSwitch
|  | Not Tested | BACnet Passthrough |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/BIN/2/selection | BACnetPassthrough
| VFD Port 1 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/1/selection | heatWheel
| VFD Port 2 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/2/selection | heatWheel
| VFD Port 3 | Not Tested | Not Used |  |  | Radio Button | ny |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | none
|  | Not Tested | Supply Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | supplyFan
|  | Not Tested | Return Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | returnFan
|  | Not Tested | Exhaust Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | exhaustFan
|  | Not Tested | Condenser Fan |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | condenserFan
|  | Not Tested | Heat Wheel |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/VFD/3/selection | heatWheel
| Reheat | Dev and passed testing | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/ReheatValve/1/selection | none
|  | Dev and passed testing | Disable |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/cooling/4/ReheatValve/1/selection | reheatValve
|  | Dev and passed testing | 2800 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/ReheatValve/1/stepCount | 2800 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 3500 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/ReheatValve/1/stepCount | 3500 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | 6386 Steps |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/cooling/4/ReheatValve/1/stepCount | 6386 | Retained | [12 empty] | If facotry custom is selected, gray out all options
|  | Dev and passed testing | Facotry Custom |  |  | Radio Button | n | [5 empty] | Retained | [12 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot select any options, all are grayed out

## Air Handler Board
Section | Page | State | Feature | Dev Changes | Type | Chevron? | Topic Notes | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Air Handler Board | Count | Dev and passed testing | 1 Board |  | Radio Button | n |  | cfg/i/gc/boardCount/airHandler | 1
|  | Dev and passed testing | 2 Boards |  | Radio Button | n |  | cfg/i/gc/boardCount/airHandler | 2
| Air Handler Board 1 | Dev and passed testing | Unique ID |  | Radio Button or Status |  |  | cfg/i/gc/boards/airHandler/1/uuid | {{int}} | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
A2L Port | A2L Port 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/1/selection | none
|  | Dev and passed testing | Cabinet |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/1/selection | cabinet
|  | Dev and passed testing | Airstream |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/1/selection | airstream
| A2L Port 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/2/selection | none
|  | Dev and passed testing | Cabinet |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/2/selection | cabinet
|  | Dev and passed testing | Airstream |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/2/selection | airstream
| A2L Port 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/3/selection | none
|  | Dev and passed testing | Cabinet |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/3/selection | cabinet
|  | Dev and passed testing | Airstream |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/A2L/3/selection | airstream
VFD Ports | VFD Port 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/1/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/1/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  | This data is tied to the VFD port, make sure the PinLocation is in the topic correctly for all motor data entries | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/1/isLeadFan | false
| VFD Port 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/2/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/2/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/2/isLeadFan | false
| VFD Port 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/3/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/3/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/3/isLeadFan | false
| VFD Port 4 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/4/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/4/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/4/isLeadFan | false
| VFD Port 5 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/5/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/5/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/5/isLeadFan | false
| VFD Port 6 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/6/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/6/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/VFD/6/isLeadFan | false
Enable | X Fan Enable | Not Tested | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | none
|  | Not Tested | AHU Board X, Analog Output Y |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | airHandler/#/MOUT/*
Damper Port | Damper Port | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | none
|  | Dev and passed testing | Return Air |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  | Radio Button |  |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/selection | motorizedExhaustDamper
| Return Air End Switch | Dev and passed testing | Disabled |  | Radio Button | n | These are connected to what is selected for this damper port, topics are the same | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | true
| Exhaust Air End Switch | Dev and passed testing | Disabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | false
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/DAMPER/1/endSwitch | true
Analog Inputs | Duct Static Pressure | Dev and passed testing | Disabled |  | Radio Button | n | Why isn't this labeled as an AIN or 0-10V? Need to double check this one that it is actually supposed to be AIN1 | cfg/i/gc/boards/airHandler/1/STATIC/1/selection | none
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/STATIC/1/selection | ductStaticPressure
| Thermistor 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | none
|  | Dev and passed testing | Supply Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | saTemp
|  | Dev and passed testing | Space Temperature |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | raTemp
|  | Not Developed | Service Factor |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/1/selection | BACnetPassthrough
| Thermistor 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | none
|  | Dev and passed testing | Supply Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | saTemp
|  | Dev and passed testing | Space Temperature |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | raTemp
|  | Not Developed | Service Factor |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/THERM/2/selection | BACnetPassthrough
| 0-10V | Dev and passed testing | Not Used |  | Radio Button | n | See note above about Duct Static Pressure, is this AIN1? AIN2? | cfg/i/gc/boards/airHandler/1/AIN/1/selection | none
|  | Dev and passed testing | Exhaust Duct Static Pressure |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AIN/1/selection | exhaustDuctStaticPressure
|  | Dev and passed testing | Building Pressure |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AIN/1/selection | buildingPressure
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AIN/1/selection | BACnetPassthrough
Analog Outputs | Analog Output 1 | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | none
|  | Dev and passed testing | Modulating Chilled Water |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/selection | BACnetPassthrough
| Analog Output 2 | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | none
|  | Dev and passed testing | Modulating Chilled Water |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/2/selection | BACnetPassthrough
Mouts | Mout 1 NOTE: Override Active is missin | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/MOUT/8/selection | BACnetPassthrough
Enable | X Fan Enable | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | none
|  | Dev and failed testing | AHU Board X, Analog Output Y |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/AOUT/1/analogFanEnable | airHandler/#/MOUT/*
Binary Inputs | Binary Input 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/2/selection | BACnetPassthrough
| Binary Input 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/3/selection | BACnetPassthrough
| Binary Input 4 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/4/selection | BACnetPassthrough
| Binary Input 5 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/5/selection | BACnetPassthrough
| Binary Input 6 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/6/selection | BACnetPassthrough
| Binary Input 7 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/7/selection | BACnetPassthrough
| Binary Input 8 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/1/BIN/8/selection | BACnetPassthrough
Board 2 | Air Handler Board 2 | Dev and passed testing | Unique ID |  | Radio Button or Status |  |  | cfg/i/gc/boards/airHandler/2/uuid |  | Stratus/boardList | [ { "type": "cooling", "uuid": 997514480, "ip": "192.168.100.70" }, { "type": "heating", "uuid": 1939768950, "ip": "192.168.100.110" }, { "type": "energyRec", "uuid": 3255484410, "ip": "192.168.100.120" }, { "type": "preheat", "uuid": 1787656125, "ip": "192.168.100.80" }, { "type": "airHandler", "uuid": 3722996188, "ip": "192.168.100.50" }, { "type": "outsideAir", "uuid": 2483351480, "ip": "192.168.100.60" }, { "type": "powerComm", "uuid": 3338253850, "ip": "192.168.100.10" } ]
A2L Port | A2L Port 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/1/selection | none
|  | Dev and passed testing | Cabinet |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/1/selection | cabinet
|  | Dev and passed testing | Airstream |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/1/selection | airstream
| A2L Port 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/2/selection | none
|  | Dev and passed testing | Cabinet |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/2/selection | cabinet
|  | Dev and passed testing | Airstream |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/2/selection | airstream
| A2L Port 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/3/selection | none
|  | Dev and passed testing | Cabinet |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/3/selection | cabinet
|  | Dev and passed testing | Airstream |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/A2L/3/selection | airstream
VFD Ports | VFD Port 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/1/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/1/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/1/isLeadFan | false
| VFD Port 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/2/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/2/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/2/isLeadFan | false
| VFD Port 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/3/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/3/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/3/isLeadFan | false
| VFD Port 4 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/4/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/4/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/4/isLeadFan | false
| VFD Port 5 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/5/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/5/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/5/isLeadFan | false
| VFD Port 6 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/selection | none
|  | Dev and passed testing | Supply Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/selection | supplyFan
|  | Dev and passed testing | Return Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/selection | returnFan
|  | Dev and passed testing | Exhaust Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/selection | exhaustFan
|  | Dev and passed testing | Condenser Fan |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/selection | condenserFan
|  | Dev and passed testing | Heat Wheel |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/selection | heatWheel
| Supply Fan Overload Input | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/overloadInput | none
|  | Dev and passed testing | Overload Input 1 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/overloadInput | overload1 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
|  | Dev and passed testing | Overload Input 2 |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/overloadInput | overload2 | [12 empty] | You can only select the Overload Inputs ONCE throughout the ports. If it has been selected, gray out for remaining VFD Ports
| Supply Fan Type | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/vfdPortType | none
|  | Dev and passed testing | Communicating |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/6/vfdPortType | commFan
|  | Dev and passed testing | 0-10 |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/6/vfdPortType | analogFan
| Supply Fan 0-10 Voltage | Dev and passed testing | Min Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/analogMinVolts | {{float}}
|  | Dev and passed testing | Max Voltage |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/analogMaxVolts | {{float}}
| Motor Type | Dev and passed testing | Electromagnet Motor (EM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/isPMM | false
|  | Dev and passed testing | Permanent Magnet Motor (PMM) |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/isPMM | true
| Electromagnet Motor Rating | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/RPM
|  | Dev and passed testing | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/nameplateFreq
| Permanent Magnet Motor (PMM) | Dev and passed testing | Motor HP |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/HP
|  | Dev and passed testing | Motor RPM |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/RPM
|  | Not Developed | Service Factor |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/serviceFactor
|  | Dev and passed testing | Motor FLA |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/FLA
|  | Dev and passed testing | Drive Min Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMinFreq
|  | Dev and passed testing | Drive Max Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/driveMaxFreq
|  | Dev and passed testing | Nameplate Frequency |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/nameplateFreq
|  | Dev and passed testing | Ld |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.Ld
|  | Dev and passed testing | Lq |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.Lq
|  | Dev and passed testing | BEMF |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.BEMF
|  | Dev and passed testing | Rs |  | Setpoint |  |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/pmm.Rs
| Voltage | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 0
|  | Dev and passed testing | 208 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 208
|  | Dev and passed testing | 230 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 230
|  | Dev and passed testing | 460 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 460
|  | Dev and passed testing | 575 vac |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/motorData/motorVoltage | 575
| Lead/Lag | Dev and passed testing | Lead (default) |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/isLeadFan | true
|  | Dev and passed testing | Lag |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/VFD/6/isLeadFan | false
Damper Port | Damper Port | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | none
|  | Dev and passed testing | Return Air |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | raDamper
|  | Dev and passed testing | Return Air Bypass |  | Radio Button |  |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | rabDamper
|  | Dev and passed testing | Exhaust Air |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/selection | motorizedExhaustDamper
| Return Air End Switch | Dev and passed testing | Disabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | true
| Return Air Bypass End Switch | Dev and passed testing | Disabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | true
| Exhaust Air End Switch | Dev and passed testing | Disabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | false
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/DAMPER/2/endSwitch | true
Analog Inputs | Duct Static Pressure | Dev and passed testing | Disabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/STATIC/1/selection | none
|  | Dev and passed testing | Enabled |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/STATIC/1/selection | ductStaticPressure
| Thermistor 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | none
|  | Dev and passed testing | Supply Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | saTemp
|  | Dev and passed testing | Space Temperature |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | raTemp
|  | Not Developed | Mixed Air Temperature |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/1/selection | BACnetPassthrough
| Thermistor 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | none
|  | Dev and passed testing | Supply Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | saTemp
|  | Dev and passed testing | Space Temperature |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | spaceTemp
|  | Dev and passed testing | Space Slide Adjust |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | spaceSlideAdjust
|  | Dev and passed testing | Return Air Temp |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | raTemp
|  | Not Developed | Mixed Air Temperature |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | mixedAirTemp
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/THERM/2/selection | BACnetPassthrough
| 0-10V | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AIN/1/selection | none
|  | Dev and passed testing | Exhaust Duct Static Pressure |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AIN/1/selection | exhaustDuctStaticPressure
|  | Dev and passed testing | Building Pressure |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AIN/1/selection | buildingPressure
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AIN/1/selection | BACnetPassthrough
Analog Outputs | Analog Output 1 | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | none
|  | Dev and passed testing | Modulating Chilled Water |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/1/selection | BACnetPassthrough
| Analog Output 2 | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | none
|  | Dev and passed testing | Modulating Chilled Water |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | modulatingChilledWater
|  | Dev and passed testing | Modulating Hot Water/Steam |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | modulatingHotWater
|  | Dev and passed testing | Modulating Preheat |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | modulatingPreheat
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/AOUT/2/selection | BACnetPassthrough
Mouts | Mout 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/1/selection | BACnetPassthrough
| Mout 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/2/selection | BACnetPassthrough
| Mout 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/3/selection | BACnetPassthrough
| Mout 4 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/4/selection | BACnetPassthrough
| Mout 5 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/5/selection | BACnetPassthrough
| Mout 6 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/6/selection | BACnetPassthrough
| Mout 7 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/7/selection | BACnetPassthrough
| Mout 8 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | none
|  | Dev and passed testing | Reversing Valve |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | reversingValve
|  | Dev and passed testing | ERV |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | heatWheelEnable
|  | Dev and passed testing | Morning Warmup/Cooldown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | morningWarmup/cooldown
|  | Dev and passed testing | Low Ambient Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | lowAmbientEnable
|  | Dev and passed testing | Return Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | returnFanEnable
|  | Dev and passed testing | Exhaust Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | exhaustFanEnable
|  | Dev and passed testing | Supply Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | supplyFanEnable
|  | Dev and passed testing | Condenser Fan Enable |  | Radio Button | y |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | condenserFanEnable
|  | Dev and passed testing | Econ Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | econoActive
|  | Dev and passed testing | Occupied Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | occupiedActive
|  | Dev and failed testing | Override Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | overrideActive
|  | Dev and passed testing | Alarm Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | alarmActive
|  | Dev and passed testing | Reheat Active |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | reheatActive
|  | Dev and passed testing | Heat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | heatEnable
|  | Dev and passed testing | Cool Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | coolEnable
|  | Dev and passed testing | Preheat Enable |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | preheatEnable
|  | Dev and failed testing | Crank Case Heater | 1)Payload - field value 2)topics - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | crankCaseHeater
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/MOUT/8/selection | BACnetPassthrough
Binary Inputs | Binary Input 1 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/1/selection | BACnetPassthrough
| Binary Input 2 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | proofOfH2O
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/2/selection | BACnetPassthrough
| Binary Input 3 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | proofOfH2O
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/3/selection | BACnetPassthrough
| Binary Input 4 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/4/selection | BACnetPassthrough
| Binary Input 5 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/5/selection | BACnetPassthrough
| Binary Input 6 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/6/selection | BACnetPassthrough
| Binary Input 7 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/7/selection | BACnetPassthrough
| Binary Input 8 | Dev and passed testing | Not Used |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | none
|  | Dev and passed testing | Hood On |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | hoodOn
|  | Dev and passed testing | Remote Shutdown |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | remoteShutdown
|  | Dev and passed testing | Remote Occupied |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | remoteOccupied
|  | Dev and passed testing | Proof of Waterflow | 1)Payload - field value | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | proofOfH20
|  | Dev and passed testing | Defrost Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | defrostSwitch
|  | Dev and passed testing | Heat Wheel Rotation |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | rotationStatus
|  | Dev and passed testing | Supply Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | supplyAirflowSwitch
|  | Dev and passed testing | Return Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | returnAirflowSwitch
|  | Dev and passed testing | Exhaust Airflow Switch |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | exhaustAirflowSwitch
|  | Dev and passed testing | BACnet Passthrough |  | Radio Button | n |  | cfg/i/gc/boards/airHandler/2/BIN/8/selection | BACnetPassthrough

## Sensors
Section | Page | Status | Feature | Type | Chevron? | Topic Notes | Dev changes | Topic | Payload | Topic 2 (if required) | QA Testing - Dev build | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Space Sensor | Type | Dev and passed testing | No Space Sensor | Radio Button | n |  |  | cfg/i/gc/sensorConfig/spaceSensorType | none
|  | Dev and passed testing | Analog | Radio Button | y |  |  | cfg/i/gc/sensorConfig/spaceSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | y |  |  | cfg/i/gc/sensorConfig/spaceSensorType | digital
|  | Dev and passed testing | TS Space Sensor | Radio Button | n |  |  | cfg/i/gc/sensorConfig/spaceSensorType | tsSpace
|  | Dev and passed testing | BACnet Temp | Radio Button | n |  |  | cfg/i/gc/sensorConfig/spaceSensorType | bacnet
|  | Dev and failed testing | + Humidity | Child Checkbox | n | "bacnetHum" when checked, "bacnet" when unchecked |  | cfg/i/gc/sensorConfig/spaceSensorType | bacnetHum |  | Plus Humidity' was changed to '+ Humidity' for automation purposes
|  | Dev and failed testing | Remote Display | Checkbox | n |  |  | cfg/i/gc/sensorConfig/spaceSensorRemoteDisplay | boolean | True when selected, False when not selected | Remote Dispaly' was changed to 'Remote Display' for automation purposes
| Analog Space Sensor SP's | Dev and passed testing | # of Space Sensors | Setpoint |  |  |  | cfg/i/gc/sensorConfig/numSpaceSensors | integer | [7 empty] | N/A
|  | Dev and passed testing | Override | Setpoint |  |  |  | cfg/i/manager/spaceOverride/duration | integer | [7 empty] | Hours
|  | Dev and passed testing | Setpoint Adjustment Limit | Setpoint |  |  |  | cfg/i/manager/spaceOverride/setpointAdjust/Limit | integer | [7 empty] | F or C
| Digital Space Sensor SP's | Dev and passed testing | # of Space Sensors | Setpoint |  |  |  | cfg/i/gc/sensorConfig/numSpaceSensors | integer | [7 empty] | N/A
|  | Dev and passed testing | Override | Setpoint |  |  |  | cfg/i/manager/spaceOverride/duration | integer | [7 empty] | Hours
|  | Dev and passed testing | Setpoint Adjustment Limit | Setpoint |  |  |  | cfg/i/manager/spaceOverride/setpointAdjust/Limit | integer | [7 empty] | F or C
Return Sensor | Type | Dev and passed testing | No Return Sensor | Radio Button | n |  | Retained | cfg/i/gc/sensorConfig/returnSensorType | none
|  | Dev and passed testing | Analog | Radio Button | n |  | Retained | cfg/i/gc/sensorConfig/returnSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | n |  | Retained | cfg/i/gc/sensorConfig/returnSensorType | digital
|  | Dev and passed testing | BACnet Temp | Radio Button | n |  | Retained | cfg/i/gc/sensorConfig/returnSensorType | bacnet
|  | Dev and failed testing | Plus Humidity | Child Checkbox | n | "bacnetHum" when checked, "bacnet" when unchecked | Retained | cfg/i/gc/sensorConfig/returnSensorType | bacnetHum
Outdoor Air Sensor | Type | Dev and passed testing | No OA Sensor | Radio Button | n |  |  | cfg/i/gc/sensorConfig/oaSensorType | none
|  | Dev and passed testing | Analog | Radio Button | n |  |  | cfg/i/gc/sensorConfig/oaSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | n |  |  | cfg/i/gc/sensorConfig/oaSensorType | digital
|  | Dev and passed testing | BACnet Temp | Radio Button | n |  |  | cfg/i/gc/sensorConfig/oaSensorType | bacnet |  | BACnet Temperature' was changed to 'BACnet Temp' for automation purposes
|  | Dev and failed testing | Plus Humidity | Child Checkbox | n | "bacnetHum" when checked, "bacnet" when unchecked |  | cfg/i/gc/sensorConfig/oaSensorType | bacnetHum
|  | Dev and passed testing | Global Broadcast | Radio Button | n |  |  | cfg/i/gc/sensorConfig/oaSensorType | globalBroadcast
Supply Air Sensor | Type | Dev and passed testing | Analog | Radio Button | n |  | Retained | cfg/i/gc/sensorConfig/supplyAirSensorType | analog
|  | Dev and passed testing | Digital | Radio Button | n |  | Retained | cfg/i/gc/sensorConfig/supplyAirSensorType | digital
CO2 Sensor | Type | Dev and passed testing | None | Radio Button | n |  |  | cfg/i/gc/sensorConfig/co2SensorType | none
|  | Dev and passed testing | Digital | Radio Button | y |  |  | cfg/i/gc/sensorConfig/co2SensorType | digital
|  | Not Tested | Reads CO2 Broadcast | Radio Button | n |  |  | cfg/i/gc/sensorConfig/co2SensorType | co2Broadcast
|  | Not Tested | Reads CO2 from BACnet | Radio Button | n |  |  | cfg/i/gc/sensorConfig/co2SensorType | bacnet
| CO2 Setpoints | Not Tested | CO2 Sensor Offset | Setpoint |  |  | Retained | cfg/i/gc/sensorConfig/co2SensorOffset | float | [7 empty] | PPM
|  | Not Tested | CO2 Setpoint | Setpoint |  |  |  | sp/i/iaq | float | [7 empty] | PPM
Calibration | Space Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/space/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/space/humidity
| Return Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/ra/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/ra/humidity
| Outside Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/oa/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/oa/humidity
| Supply Sensor | Not Developed | Temp Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/sa/temp
|  | Not Developed | Humidity Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/sa/humidity
| CO2 Sensor | Not Developed | CO2 Calibration Offset | Setpoint |  |  |  | cfg/i/sensor/offset/sts/i/space/co2

## OA Damper
Section | Page | State | Feature | Type | Chevron? | Topic Notes | Dev chnages | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Config | OA Config | Dev and passed testing | No Economizer Control | Radio Button | n |  |  | cfg/i/manager/economizerControl | none
|  | Dev and passed testing | Standard Economizer Control | Radio Button | n |  |  | cfg/i/manager/economizerControl | standard
|  | Dev and passed testing | Economizer Control with IAQ Override | Radio Button | y |  |  | cfg/i/manager/economizerControl | iaq
|  | Dev and passed testing | Building Pressure Control | Radio Button | y |  | Retained | cfg/i/pressureRelief | OADBuildingPressure
|  | Dev and failed testing | Allow Economizer During Unoccupied Mode | Radio Button | n |  |  | cfg/i/manager/unoccEconoEnable | boolean
|  | Dev and failed testing | Fault Detection Diagnostics | Radio Button | n |  |  | cfg/i/economizer/faultDetectionDiagnostics | boolean
Min Pos | Min Pos | Dev and passed testing | Minimum Economizer Position | Setpoint |  |  |  | cfg/oa/damper/minPosition | integer | [6 empty] | % | 0 | 100 | 10 | Enter the desired minimum outdoor air damper position for fresh air requirements during occupied times. The Economizer damper will be allowed to modulate up from this minimum position to 100% outdoor air as needed for cooling or CO2 demand control ventilation but will not go below. The economizer must be configured and the unit must be in Occupied Mode for all HVAC applications.
Enable | OA Damper Enable | Dev and passed testing | Outside Air Drybulb | Radio Button | y |  |  | cfg/economizeEnableMethod | OADrybulb
|  | Dev and passed testing | Outside Air Wetbulb | Radio Button | y |  |  | cfg/economizeEnableMethod | OAWetbulb
|  | Dev and passed testing | Outside Air Dewpoint | Radio Button | y |  |  | cfg/economizeEnableMethod | OADewpoint
|  | Dev and failed testing | Comparative w/ Drybulb Limit | Radio Button | y |  |  | cfg/economizeEnableMethod | ComparativeEnthalpyDryBulb
|  | Dev and failed testing | Comparative Enthalpy | Radio Button | y |  |  | cfg/economizeEnableMethod | ComparativeEnthalpy
| OA Drybulb | Dev and passed testing | OA Enable Setpoint | Setpoint |  |  |  | cfg/economizeSetpoint | integer | [6 empty] | F or C | -30 | 80 | 55 | This is the setpoint in which the unit will enter the economizer mode based on the enable selection i.e. dry bulb, wet bulb, dewpoint, comparative enthalpy, or comparative w/ dry bulb limit.
| OA Wetbulb | Dev and passed testing | OA Enable Setpoint | Setpoint |  |  |  | cfg/economizeSetpoint | integer | [6 empty] | F or C | -30 | 80 | 55 | This is the setpoint in which the unit will enter the economizer mode based on the enable selection i.e. dry bulb, wet bulb, dewpoint, comparative enthalpy, or comparative w/ dry bulb limit.
| OA Dewpoint | Dev and passed testing | OA Enable Setpoint | Setpoint |  |  |  | cfg/economizeSetpoint | integer | [6 empty] | F or C | -30 | 80 | 55 | This is the setpoint in which the unit will enter the economizer mode based on the enable selection i.e. dry bulb, wet bulb, dewpoint, comparative enthalpy, or comparative w/ dry bulb limit.
| Comparative Enthalpy w/ Drybulb Limit | Dev and passed testing | OA Limit Setpoint | Setpoint |  |  |  | cfg/economizeSetpoint | integer | [6 empty] | F or C
|  | Dev and passed testing | OA Enthalpy Setpoint | Setpoint |  |  |  | cfg/economizeEnthalpySetpoint | integer | [6 empty] | BTU/lb | 12 | 35 | 28 | This the Enthalpy Enable Setpoint for Comparative Enthalpy Economizer Operation.
|  | Dev and passed testing | Enthalpy Deadband | Setpoint |  |  |  | cfg/economizeEnthalpyDeadband | float | [6 empty] | BTU/lb | 0.3 | 15 | 0.5 | This the Enthalpy Enable Deadband for Comparative Enthalpy Economizer Operation.
| Comparative Enthalpy w/ Drybulb Limit | Dev and passed testing | OA Enthalpy | Setpoint |  |  |  | cfg/economizeEnthalpySetpoint | integer | [6 empty] | BTU/lb
|  | Dev and passed testing | Enthalpy Deadband | Setpoint |  |  |  | cfg/economizeEnthalpyDeadband | float | [6 empty] | BTU/lb
Voltages | Voltages | Dev and passed testing | Minimum Economizer Voltage | Setpoint |  |  |  | cfg/i/economizer/voltage/min | integer | [6 empty] | VDC | 0 | 10 | 10 | Enter the maximum voltage for economizer full open position.
|  | Dev and passed testing | Maximum Economizer Voltage | Setpoint |  |  |  | cfg/i/economizer/voltage/max | integer | [6 empty] | VDC | 0 | 10 | 0 | Enter the minimum voltage for economizer full closed position.

## Dehum
Section | Page | Status | Feature | Dev Changes | Dev status | Type | Chevron? | Topic Notes | Topic UI Topic | Topic UI Payload | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Config | Config | Dev and failed testing | No Dehum | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | n |  | ui/cfg/dehum/config | noDehum | cfg/i/dehum/enabled | false
|  | Dev and failed testing | Humidity Control | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/dehum/config | humidity | cfg/i/dehum/usesDewpoint | false | cfg/i/dehum/enabled | true
|  | Dev and failed testing | Dewpoint Control | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y |  | ui/cfg/dehum/config | dewpoint | cfg/i/dehum/usesDewpoint | true | cfg/i/dehum/enabled | true
|  | Dev and failed testing | Enable Dehum in All Unit Operations | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | n |  | ui/cfg/dehum/config | enableOption | cfg/i/dehum/enabled | true
|  | Can't Test | Vent (standard mode only) | Commented and hidden |  | Checkbox | y |  | ui/cfg/dehum/enable | vent | cfg/i/dehum/priority/vent
|  | Can't Test | Cool | Commented and hidden |  | Child Checkbox | n |  | ui/cfg/dehum/enable | cool | cfg/i/dehum/priority/cooling
|  | Can't Test | Heat | Commented and hidden |  | Child Checkbox | n |  | ui/cfg/dehum/enable | heat | cfg/i/dehum/priority/heating
|  | Not Tested | Unoccupied |  |  | Child Checkbox | n |  | ui/cfg/dehum/enable | unoccupied | cfg/i/dehum/whileUnoccupied | true
| Enable Sensor | Dev and failed testing | No Enable Sensor |  |  | Radio Button | n |  |  |  | cfg/i/dehum/enableSensor | none
|  | Dev and failed testing | Space Sensor |  |  | Radio Button | y | Even when sensor is selected, can't be selected |  |  | cfg/i/dehum/enableSensor | Space |  |  |  |  | Must Configure Space Sensor
|  | Dev and failed testing | Return Sensor |  |  | Radio Button | y | Even when sensor is selected, can't be selected |  |  | cfg/i/dehum/enableSensor | Return |  |  |  |  | Must Configure Return Sensor
|  | Dev and failed testing | OA Sensor |  |  | Radio Button | y | Even when sensor is selected, can't be selected |  |  | cfg/i/dehum/enableSensor | OA |  |  |  |  | Must Configure OA Sensor
|  | Dev and failed testing | Supply Air Dewpoint Control (Sensor Must Use Digital Temp/Hum) |  |  | Child Checkbox | y |  |  |  | cfg/i/dehum/supplyAirDewpointControl/enable | true/false |  |  |  |  | Sensor must use Digital Temp/Hum
| Humidity Setpoints | Not Tested | Humidity Setpoint |  |  | Setpoint |  |  |  |  | sp/i/rhCoolSPLo | integer | [6 empty] | % | 0 | 100 | 50
|  | Not Tested | Humidity OAT Lockout |  |  | Setpoint |  |  |  |  | cfg/i/dehum/oatLockout | integer | [6 empty] | F or C | -30 | 110 | 60
| Dewpoint Setpoints | Can't Test | Dewpoint Setpoint |  |  | Setpoint |  |  |  |  | sp/i/dpSPLo | [7 empty] | F or C | 0 | 110 | 50
|  | Not Developed | Dewpoint OAT Lockout |  |  | Setpoint |  |  |  |  | cfg/i/dehum/oatLockout | integer | [6 empty] | F or C | -30 | 110 | 60
| Supply Air Dewpoint Setpoint | Can't Test | Supply Air Dewpoint Setpoint |  |  | Setpoint |  |  |  |  | sp/i/supplyAirDewpointControl/setpoint | [7 empty] | F or C
Reheat | Reheat Config | Dev and failed testing | No Reheat |  |  | Radio Button | n | Unnecessary, if there's a reheat valve assigned to the circuit, we have Modulating HGR reheat by default. Really we just need a choice between none, aux, and unit Heat. Likewise, if a Return Bypass is configured, we will use that |  |  | cfg/i/refrig/reheat/additionalSource | none
|  | Can't Test | Modulating HGR |  |  | Radio Button | y
|  | Not Developed | No Additional Reheat |  |  | Child Radio | n |  |  |  | cfg/i/refrig/reheat/additionalSource | none
|  | Dev and failed testing | Plus Aux Heat (Heat Pump Required) | Retained |  | Child Radio | n |  |  |  | cfg/i/refrig/reheat/additionalSource | Aux |  |  |  |  | Must Configure Heat Pump
|  | Dev and failed testing | Plus Unit Heat (call factory) |  |  | Child Radio | y |  |  |  | cfg/i/refrig/reheat/additionalSource | UnitHeat |  |  |  |  | Call Factory
|  | Dev and failed testing | Unit Heat for Reheat | Retained |  | Radio Button | n |  |  |  | cfg/i/refrig/reheat/additionalSource | UnitHeat
|  | Can't Test | On/Off |  |  | Radio Button | n
|  | Can't Test | Plus Unit Heat |  |  | Child Checkbox | y
|  | Can't Test | Has Return Bypass Control |  |  | Checkbox | n
|  | Can't Test | SAT Control |  |  | Child Checkbox | n
| Flush | Dev and failed testing | Enable Startup Flush |  |  | Checkbox | n |  |  |  | cfg/i/reheatFlush/enableStartupFlush | true
|  | Dev and failed testing | Enable Reheat Flush |  |  | Checkbox | y |  |  |  | cfg/i/reheatFlush/enableReheatFlush | true
|  | Dev and failed testing | Enable Condenser Flush |  |  | Checkbox | y |  |  |  | cfg/i/reheatFlush/enableOutdoorFlush | true
|  | Dev and failed testing | Enable Cooling Flush |  |  | Checkbox | y |  |  |  | cfg/i/reheatFlush/enableCoolingFlush | true
| Reheat Flush Int | Dev and failed testing | Reheat Flush Interval |  |  | Setpoint |  |  |  |  | cfg/i/reheatFlush/reheatIntervalTime
| Cond Flush Int | Dev and failed testing | Condenser Flush Interval |  |  | Setpoint |  |  |  |  | cfg/i/reheatFlush/condenserIntervalTime
| Cool Flush Int | Dev and failed testing | Cooling Flush Interval |  |  | Setpoint |  |  |  |  | cfg/i/reheatFlush/coolIntervalTime
| Valves | Can't Test | 2800 Steps |  |  | Radio Button | n |  |  |  | pcfg/i/systemConfig/_/unitConfig/refrigerationSystem/circuits/A/Reheat/interface/stepCount
|  | Can't Test | 3500 Steps |  |  | Radio Button | n |  |  |  | pcfg/i/systemConfig/_/unitConfig/refrigerationSystem/circuits/A/Reheat/interface/stepCount
|  | Can't Test | 6386 Steps |  |  | Radio Button | n |  |  |  | pcfg/i/systemConfig/_/unitConfig/refrigerationSystem/circuits/A/Reheat/interface/stepCount
|  | Can't Test | Facotry Custom |  |  | Radio Button | n | [17 empty] | ONLY selectable in Facotry mode... IF this is selected in factory mode, then users cannot

## Building Pressure
Section | Page | Status | Feature | Dev Changes | Dev status | Type | Chevron? | UI Topics | UI Topic Payload | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Type | Building Pressure Type | Not Developed | Building Pressure Sensor | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y | ui/config/buildingPressureType | buildingPressureSensor
|  | Not Developed | Duct Static Pressure | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y | ui/config/buildingPressureType | ductStaticPressure
|  | Not Developed | Fan Tracking | 1)Payloads - field value 2)topics - field value 3)UI topic is retained | working | Radio Button | y | ui/config/buildingPressureType | fanTracking | cfg/i/pressureRelief | ReturnFollowSupply
Building Pressure | Building Pressure Control | Dev and passed testing | Supply Fan |  |  | Radio Button | y |  |  | cfg/i/pressureRelief | SupplyFanBuildingPressure |  |  |  |  | Must Configure Supply Fan
|  | Dev and passed testing | Return Fan |  |  | Radio Button | y |  |  | cfg/i/pressureRelief | ReturnFanBuildingPressure |  |  |  |  | Must Configure Return Fan
|  | Not Developed | Plus Exhaust Damper |  |  | Child Checkbox | y |  |  | cfg/i/returnFanBuildingPressure/exhaustDamper/enable | true/false |  |  |  |  | Must Configure Return Fan
|  | Dev and passed testing | Exhaust Fan |  |  | Radio Button | y |  |  | cfg/i/pressureRelief | ExhaustFanBuildingPressure |  |  |  |  | Must Configure Exhaust Fan
|  | Dev and passed testing | Outside Air Damper |  |  | Radio Button | y |  |  | cfg/i/pressureRelief | OADBuildingPressure |  |  |  |  | Must Configure OA Damper
|  | Dev and passed testing | Exhaust Damper |  |  | Radio Button | y |  |  | cfg/i/pressureRelief | ExhaustDamperBuildingPressure
| SF Building Pressure Setpoints | Dev and passed testing | Building Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Dev and passed testing | Building Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Building Pressure - Return Fan Control | Can't Test | On/Off |  |  | Radio Button | n
|  | Can't Test | Modulating |  |  | Radio Button | n
| RF Building Pressure Setpoints | Dev and passed testing | Building Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Dev and passed testing | Building Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Plus Exhaust Damper Setpoints | Dev and passed testing | Exhaust Damper Setpoint |  |  | Setpoint |  |  |  | sp/i/exhaust/damper/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 0.2 | 0.1
|  | Dev and passed testing | Exhaust Damper Deadband |  |  | Setpoint |  |  |  | sp/i/exhaust/damper/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01
| Building Pressure - Exhaust Fan Control | Can't Test | On/Off |  |  | Radio Button | n
|  | Can't Test | Modulating |  |  | Radio Button | n
| EF Building Pressure Setpoints | Dev and passed testing | Building Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Dev and passed testing | Building Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| OA Damper Building Pressure Setpoints | Dev and passed testing | Building Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Dev and passed testing | Building Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Exhaust Damper Building Pressure Setpoints | Dev and passed testing | Building Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/buildingPressureSP | float | [6 empty] | "WG | -0.2 | 3 | 0.02 | Enter the desired building pressure to be maintained by the unit. The unit will adjust accordingly based on the selected building control strategy.
|  | Dev and passed testing | Building Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/buildingPressureDB | float | [6 empty] | "WG | 0.01 | 0.1 | 0.01 | Enter the acceptable tolerance from setpoint the building pressure shall be allowed to remain without making any adjustments.
| Building Pressure Sensor Type | Dev and passed testing | None |  |  | Radio Button | n |  |  | cfg/i/gc/sensorConfig/buildingPressureSensorType | none
|  | Dev and passed testing | Analog |  |  | Radio Button | n |  |  | cfg/i/gc/sensorConfig/buildingPressureSensorType | analog
|  | Can't Test | Exhaust Fan |  |  | Radio Button | n |  |  | ??
|  | Can't Test | Outside Air Damper |  |  | Radio Button | n |  |  | ??
Duct Static Pressure Sensor | Duct Static Type | Dev and passed testing | Return Fan |  |  | Checkbox | y |  |  | cfg/i/ductStaticControl/return/enabled | true/false
|  | Dev and passed testing | Exhaust Fan |  |  | Checkbox | y |  |  | cfg/i/ductStaticControl/exhaust/enabled | true/false
| RF Duct Static Setpoints | Dev and passed testing | Duct Static Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the return/exhaust fan. The return/exhaust fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and passed testing | Duct Static Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.01 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
| EF Duct Static Setpoints | Dev and passed testing | Duct Static Pressure Setpoint |  |  | Setpoint |  |  |  | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the return/exhaust fan. The return/exhaust fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and passed testing | Duct Static Pressure Deadband |  |  | Setpoint |  |  |  | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.01 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
Fan Tracking | Type | Dev and passed testing | Return Fan |  |  | Checkbox | y |  |  | cfg/i/returnFollowSupply/return/enabled | true/false
|  | Dev and passed testing | Exhaust Fan |  |  | Checkbox | y |  |  | cfg/i/returnFollowSupply/exhaust/enabled | true/false
| Return Fan Tracking | Dev and passed testing | Tracking Percent |  |  | Setpoint |  | Graham to check |  | cfg/i/returnFollowSupply/scaling | [7 empty] | % | 0 | 125 | 100 | The return fan will track the supply fan at this percentage.
|  | Dev and passed testing | Return Fan Minimum Fan Speed |  |  | Setpoint |  | Graham to check |  | cfg/i/returnFollowSupply/min | [7 empty] | % | 0 | 100 | 0 | The return fan is allowed to modulate down to this speed
| Exhaust Fan Tracking | Dev and passed testing | Tracking Percent |  |  | Setpoint |  | Graham to check |  | cfg/i/exhaustFollowSupply/scaling | [7 empty] | % | 0 | 125 | 100 | The exhaust fan will track the supply fan at this percentage.
|  | Dev and passed testing | Exhaust Fan Minimum Fan Speed |  |  | Setpoint |  | Graham to check |  | cfg/i/exhaustFollowSupply/min | [7 empty] | % | 0 | 100 | 0 | The exhaust fan is allowed to modulate down to this speed.

## Filters
Section | Page | Status | Feature | Type | Dev changes | Chevron? | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Filters | Type | Can't Test | Pre | Checkbox |  | y
|  | Can't Test | Main | Checkbox |  | y
|  | Can't Test | Return Air Bypass | Checkbox |  | y
|  | Can't Test | Heat Wheel OA | Checkbox |  | y | [6 empty] | Must Configure Heat Wheel Board
|  | Can't Test | Heat Wheel Exhaust | Checkbox |  | y | [6 empty] | Must Configure Heat Wheel Board
|  | Can't Test | Preheat | Checkbox |  | y | [6 empty] | Must Configure Preheat
Pre | Pre Monitoring Type | Can't Test | Binary | Radio Button |  | n
|  | Can't Test | Differential Pressure | Radio Button |  | y
|  | Can't Test | Change Interval | Radio Button |  | y
| Pre Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint | [10 empty] | " WG
|  | Can't Test | Filter Replaced | Button
| Pre Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Lifespan | Setpoint | [10 empty] | days
|  | Can't Test | Filter Replaced | Button
Main | Main Monitoring Type | Can't Test | Binary | Radio Button |  | n
|  | Can't Test | Differential Pressure | Radio Button |  | y
|  | Can't Test | Change Interval | Radio Button |  | y
| Main Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint | [10 empty] | " WG
|  | Can't Test | Filter Replaced | Button
| Main Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Lifespan | Setpoint | [10 empty] | days
|  | Can't Test | Filter Replaced | Button
Return Air Bypass | Return Air Bypass Monitoring Type | Can't Test | Binary | Radio Button |  | n
|  | Can't Test | Differential Pressure | Radio Button |  | y
|  | Can't Test | Change Interval | Radio Button |  | y
| Return Air Bypass Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  |  | sts/i/filters/ra/1/pressure/filterLifeRemaining | 100 | [6 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint | Retained |  | cfg/i/filters/ra/1/pressure/airFilterDPThreshold | [7 empty] | " WG
|  | Can't Test | Filter Reset | Button |  |  | ctrl/i/filters/ra/1/filterReplaced | []
| Return Air Bypass Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  |  | sts/i/filters/ra/1/timer/lifeTimeRemaining | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint | Retained |  | cfg/i/filters/ra/1/timer/filterLifespan | [7 empty] | days
|  | Can't Test | Filter Reset | Button |  |  | ctrl/i/filters/ra/1/filterReplaced
Heat Wheel OA | Heat Wheel OA Monitoring Type | Can't Test | Binary | Radio Button |  | n
|  | Can't Test | Differential Pressure | Radio Button |  | y
|  | Can't Test | Change Interval | Radio Button |  | y
| Heat Wheel OA Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint | [10 empty] | " WG
|  | Can't Test | Filter Replaced | Button
| Heat Wheel OA Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Lifespan | Setpoint | [10 empty] | days
|  | Can't Test | Filter Replaced | Button
Heat Wheel Exhaust | Heat Wheel Exhaust Monitoring Type | Can't Test | Binary | Radio Button |  | n
|  | Can't Test | Differential Pressure | Radio Button |  | y
|  | Can't Test | Change Interval | Radio Button |  | y
| Heat Wheel Exhaust Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint | [10 empty] | " WG
|  | Can't Test | Filter Replaced | Button
| Heat Wheel Exhaust Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status | [10 empty] | days
|  | Can't Test | Lifespan | Setpoint | [10 empty] | days
|  | Can't Test | Filter Replaced | Button
Preheat | Preheat Monitoring Type | Can't Test | Binary | Radio Button |  | n
|  | Can't Test | Differential Pressure | Radio Button |  | y
|  | Can't Test | Change Interval | Radio Button |  | y
| Preheat Filter Differential Setpoints | Can't Test | Lifetime Remaining | Status |  |  | sts/i/filters/preheat/1/pressure/filterLifeRemaining | [7 empty] | days
|  | Can't Test | Differential Pressure Threshold | Setpoint | Retained |  | cfg/i/filters/preheat/1/pressure/airFilterDPThreshold | [7 empty] | " WG
|  | Can't Test | Filter Replaced | Button |  |  | ctrl/i/filters/preheat/1/filterReplaced
| Preheat Filter Timeout Setpoints | Can't Test | Lifetime Remaining | Status |  |  | sts/i/filters/preheat/1/timer/lifeTimeRemaining | [7 empty] | days
|  | Can't Test | Lifespan | Setpoint | Retained |  | cfg/i/filters/preheat/1/timer/filterLifespan | [7 empty] | days
|  | Can't Test | Filter Replaced | Button |  |  | ctrl/i/filters/preheat/1/filterReplaced

## ERV
Section | Page | Status | Feature | Type | Chevron? | Topic Notes | Dev changes | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Type | Type | Dev and passed testing | On/Off | Radio Button | n |  |  | cfg/i/gc/fanConfig/heatWheel/controlMethod | OnOff
|  | Dev and passed testing | Modulating | Radio Button | y |  |  | cfg/i/gc/fanConfig/heatWheel/controlMethod | Modulating
| Modulating ERV | Can't Test | 0-10V | Radio Button | y | This should not be defined here, it should be defined at the board level now, as we do with all other VFDs/analogs
|  | Can't Test | Communicating | Radio Button | n
| Modulating ERV Setpoints | Can't Test | ERV Min Voltage | Setpoint | [11 empty] | vdc
|  | Can't Test | ERV Max Voltage | Setpoint | [11 empty] | vdc
Disables | ERV Disables | Dev and passed testing | Economizer | Radio Button | n |  | Retained | cfg/i/heatWheel/enableMethod | EconoAtMin
|  | Dev and passed testing | OA Enthalpy | Radio Button | y |  | Retained | cfg/i/heatWheel/enableMethod | OAEnthalpy |  |  |  |  | Must configure Digital or BACnet OA Sensor
| ERV OA Enthalpy Setpoints | Dev and passed testing | Low OA Enthalpy Setpoint | Setpoint |  |  |  | sp/i/heatWheel/enable/outdoorEnthalpy/low | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | High OA Enthalpy Setpoint | Setpoint |  |  |  | sp/i/heatWheel/enable/outdoorEnthalpy/high | {{float}} | [6 empty] | F or C
Bypass | ERV Bypass Type | Dev and passed testing | On/Off | Radio Button | n |  |  | cfg/i/gc/fanConfig/heatWheel/ERVBypassType | OnOff
|  | Dev and passed testing | Modulating | Radio Button | y |  |  | cfg/i/gc/fanConfig/heatWheel/ERVBypassType | Modulating
| Modulating ERV Bypass Setpoints | Dev and passed testing | OA ERV Bypass Min | Setpoint |  | UI label wrong |  | cfg/i/gc/fanConfig/heatWheel/oaERVBypassMin | {{float}} | [6 empty] | vdc
|  | Dev and passed testing | Exhaust ERV Bypass Min | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/ExhaustERVBypassMin | {{float}} | [6 empty] | vdc
|  | Dev and passed testing | OA ERV Bypass Max | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/oaERVBypassMax | {{float}} | [6 empty] | vdc
|  | Dev and passed testing | Exhaust ERV Bypass Max | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/ExhaustERVBypassMax | {{float}} | [6 empty] | vdc
|  | Dev and passed testing | OA Differnetial Pressure | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/OADifferentialPressure | {{float}} | [6 empty] | "WG
|  | Dev and passed testing | Exhaust Differential Pressure | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/ExhaustDifferentialPressure | {{float}} | [6 empty] | "WG
Defrost | Defrost | Dev and passed testing | No Defrost | Radio Button | n |  |  | cfg/i/gc/fanConfig/heatWheel/defrostEnabled | false
|  | Dev and passed testing | Defrost Enable | Radio Button | y |  |  | cfg/i/gc/fanConfig/heatWheel/defrostEnabled | true
| ERV Defrost Setpoints | Dev and passed testing | OA Temperature | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/defrostTemp | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | OA Dewpoint | Setpoint |  |  |  | cfg/i/gc/fanConfig/heatWheel/defrostDewpoint | {{float}} | [6 empty] | F or C

## Preheat
Section | Section | Page | Status | Feature | Type | Chevron? | Topic | Payload | Dev changes | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Preheat Type | Preheat | Type | Dev and passed testing | None | Radio Button | n | cfg/i/gc/heatConfig/preheatConfig/heatType | none | Retained
|  |  | Dev and passed testing | Electric | Radio Button | y | cfg/i/gc/heatConfig/preheatConfig/heatType | electric | Retained
|  |  | Dev and passed testing | Water/Steam | Radio Button | y | cfg/i/gc/heatConfig/preheatConfig/heatType | water | Retained
|  | Electric Setpoints | Dev and passed testing | Stage Up Window | Setpoint |  | cfg/i/gc/heatConfig/preheatConfig/stageUpWindow | {{float}} | Retained | [6 empty] | F or C | 1 | 15 | 3
|  |  | Dev and passed testing | Stage Down Window | Setpoint |  | cfg/i/gc/heatConfig/preheatConfig/stageDownWindow | {{float}} | Retained | [6 empty] | F or C | 1 | 15 | 3
|  |  | Dev and passed testing | Stage Up Timer | Setpoint |  | cfg/i/gc/heatConfig/preheatConfig/stageUpTimerMinutes | {{int}} | Retained | [6 empty] | Min
|  |  | Dev and passed testing | Stage Down Timer | Setpoint |  | cfg/i/gc/heatConfig/preheatConfig/stageDownTimerMinutes | {{int}} | Retained | [6 empty] | Min
|  | Water/Steam Setpoints | Dev and passed testing | Min Voltage | Setpoint |  | cfg/i/gc/heatConfig/preheatConfig/minWaterVolts | {{float}} | Retained | [6 empty] | VDC
|  |  | Dev and passed testing | Max Voltage | Setpoint |  | cfg/i/gc/heatConfig/preheatConfig/maxWaterVolts | {{float}} | Retained | [6 empty] | VDC
|  | Preheat Setpoints | Dev and passed testing | OAT Enable Setpoint | Setpoint |  | sp/i/preheatEnableTemp | {{float}} | [7 empty] | F or C | -30 | 105 | 30
|  |  | Dev and passed testing | Cool Leaving Air Setpoint | Setpoint |  | sp/i/preheat/LATSP/cool | {{float}} | [7 empty] | F or C | 0 | 90 | 45
|  |  | Dev and passed testing | Heat Leaving Air Setpoint | Setpoint |  | sp/i/preheat/LATSP/heat | {{float}} | [7 empty] | F or C | 0 | 140 | 45
|  |  | Dev and passed testing | Vent Leaving Air Setpoint | Setpoint |  | sp/i/preheat/LATSP/vent | {{float}} | [7 empty] | F or C | 0 | 90 | 45

## Heating
Section | Page | Status | Feature | Dev Changes | dev status | Type | Chevron? | Topic Notes | UI Topic | UI Payload | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Heating | Heat Type | Dev and failed testing | None | 1)Payloads - field value 2)topics - field value 3)retain UI topic & topic 2 |  | Radio Button | n |  | ui/config/heatConfig/heatType | none | cfg/i/gc/heatConfig/heatType | none | cfg/i/gc/heatConfig/isHeatpump | false
|  | Dev and failed testing | Heat Pump | 1)Payloads - field value 2)topics - field value 3)retain UI topic & topic 2 | working | Radio Button | y |  | ui/config/heatConfig/heatType | heatPump | cfg/i/gc/heatConfig/heatType | none | cfg/i/gc/heatConfig/isHeatpump | true
|  | Dev and failed testing | Gas | 1)Payloads - field value 2)topics - field value 3)retain UI topic & topic 2 | working | Radio Button | y |  | ui/config/heatConfig/heatType | gas | cfg/i/gc/heatConfig/heatType | gas | cfg/i/gc/heatConfig/isHeatpump | false
|  | Dev and passed testing | Heating Tempering |  |  | Child Checkbox | n |  | ui/config/heatConfig/heatTempering | boolean | cfg/i/manager/supplyAirTempering/enable | true
|  | Dev and failed testing | Electric | 1)Payloads - field value 2)topics - field value 3)retain UI topic & topic 2 | working | Radio Button | y |  | ui/config/heatConfig/heatType | electric | cfg/i/gc/heatConfig/heatType | electric | cfg/i/gc/heatConfig/isHeatpump | false
|  | Dev and failed testing | Water/Steam | 1)Payloads - field value 2)topics - field value 3)retain UI topic & topic 2 |  | Radio Button | y | NYI | ui/config/heatConfig/heatType | water | cfg/i/gc/heatConfig/heatType | water | cfg/i/gc/heatConfig/isHeatpump | false
|  | Not Tested | Direct Fire | Commented and hidden |  | Radio Button | y | NYI | ui/config/heatConfig/heatType | directFire | cfg/i/gc/heatConfig/heatType | directFire | cfg/i/gc/heatConfig/isHeatpump | false
| Setpoints | Dev and passed testing | Stage Up Window |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/stageUpWindow | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Stage Down Window |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/stageDownWindow | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Stage Up Timer |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/stageUpTimerMinutes | {{int}} | [6 empty] | min
|  | Dev and passed testing | Stage Down Timer |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/stageDownTimerMinutes | {{int}} | [6 empty] | min
|  | Dev and passed testing | Min Run Time |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/minRunTime | {{int}} | [6 empty] | min
|  | Dev and passed testing | Min Off Time |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/minOffTime | {{int}} | [6 empty] | min
|  | Dev and passed testing | Heating OAT Lockout |  |  | Setpoint |  |  |  |  | cfg/i/activeHeating/oatLockout | {{float} | [6 empty] | F or C
|  | Dev and passed testing | Heat SAT Setpoint |  |  | Setpoint |  |  |  |  | sp/i/saTempHeatSP/max | {{float}} | [6 empty] | F or C |  |  | 150
|  | Dev and passed testing | High SAT Cutoff |  |  | Setpoint |  |  |  |  | cfg/i/supplyAirTempCutoffHigh | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Heating Min Fan Speed |  |  | Setpoint |  |  |  |  | cfg/i/SZVAV/fanHeatMinSpeed | {{float}} | [6 empty] | min
|  | Dev and passed testing | Heat Control Window |  |  | Setpoint |  |  |  |  | cfg/i/manager/heating/controlWindow | {{float}} | [6 empty] | %
|  | Dev and passed testing | Heating Max Fan Speed |  |  | Setpoint |  |  |  |  | cfg/i/SZVAV/fanHeatMaxSpeed | {{float}} | [6 empty] | %
|  | Dev and failed testing | Changeover Delay Time |  |  | Setpoint |  |  |  |  | cfg/i/oppositeModeLockoutTime | {{float in seconds}}
Heat Pump | Type | Dev and passed testing | Air Source | UI Topic and payload added |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.heatPumpType | air
|  | Dev and passed testing | Water |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.heatPumpType | water
| WHP Glycol | Dev and passed testing | 0% (32.0°F / 0°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 5% (29.1°F / -1.6°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 10% (26.1°F / -3.3°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 15% (22.9°F / -5.1°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 20% (19.2°F / -7.1°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 25% (14.7°F / -9.6°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 30% (9.2°F / -12.7°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 35% (2.4°F / -16.4°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
|  | Dev and passed testing | 40% (-6.0°F / -21.1°C Freezing Point) |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.glycol | {{int 0~100}}
| Reversing Valve Type | Dev and passed testing | Fail to Heating |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.revValveFailTo | heat
|  | Dev and passed testing | Fail to Cooling |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.revValveFailTo | cool
| Aux/Emergency Heat | Dev and passed testing | None | 1)UI Topic and payload added |  | Radio Button | n |  | ui/config/heatConfig/auxEmergencyHeat | none | cfg/i/gc/heatConfig/heatType | none
|  | Dev and passed testing | Gas | 1)UI Topic and payload added |  | Radio Button | n |  | ui/config/heatConfig/auxEmergencyHeat | gas | cfg/i/gc/heatConfig/heatType | gas
|  | Dev and passed testing | Heating Tempering |  |  | Child Checkbox | n |  | ui/config/heatConfig/auxEmergencyHeat/heatTempering | boolean | cfg/i/manager/supplyAirTempering/enable | true
|  | Dev and passed testing | Aux Heat | 1)UI Topic and payload added |  | Child Radio Button | y |  | ui/config/heatConfig/auxEmergencyHeat/gasAsAux | auxHeat | cfg/i/gc/heatConfig/gasAsAux | true | [12 empty] | To be able to select this, the simultaneous heat/cool in Unit Settings must be enabled.
|  | Dev and passed testing | Emergency Heat | 1)UI Topic and payload added |  | Child Radio Button | y |  | ui/config/heatConfig/auxEmergencyHeat/gasAsAux | emergencyHeat | cfg/i/gc/heatConfig/gasAsAux | false | [12 empty] | To be able to select this, the simultaneous heat/cool in Unit Settings must be enabled.
|  | Dev and passed testing | Electric | 1)UI Topic and payload added |  | Radio Button | y |  | ui/config/heatConfig/auxEmergencyHeat | electric | cfg/i/gc/heatConfig/heatType | electric
|  | Dev and passed testing | Water/Steam | 1)UI Topic and payload added |  | Radio Button | y |  | ui/config/heatConfig/auxEmergencyHeat | water | cfg/i/gc/heatConfig/heatType | water
| Gas - Heat Boards | Dev and failed testing | Heat Board 1 Unique ID |  |  | Button/Status |  |  |  |  | cfg/i/gc/boards/heating/1/uuid | {{int}} | [12 empty] | Show number of boards selected in board section
|  | Dev and failed testing | Heat Board 2 Unique ID |  |  | Button/Status |  |  |  |  | cfg/i/gc/boards/heating/2/uuid | {{int}} | [12 empty] | If not configured for 2 boards, do not show.
| Ignition Control Board 1 | Unknown
| Ignition Control Board 1 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/0/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y | Where in the UI??
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Dev and passed testing | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Dev and passed testing | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/0/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 2 | Unknown
| Ignition Control Board 1 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/1/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/1/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 3 | Unknown
| Ignition Control Board 3 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/2/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/2/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 4 | Unknown
| Ignition Control Board 4 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/3/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/3/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 5 | Unknown
| Ignition Control Board 5 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/4/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/4/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 6 | Unknown
| Ignition Control Board 6 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/5/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/5/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 7 | Unknown
| Ignition Control Board 7 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/6/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/6/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 8 | Unknown
| Ignition Control Board 8 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/7/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board. Gray out option and throw validation message if they try to select it
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/7/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
Unknown
| Electric - Heat Boards | Not Tested | Heat Board 1 Unique ID |  |  | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/1/uuid | {{int}}
|  | Not Tested | Heat Board 2 Unique ID |  |  | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/2/uuid | {{int}}
| Heat Enable Mouts | Unknown | Mouts (PLEASE READ NOTES) |  |  | Menu Button(s) | [18 empty] | From Heating board, if there are no heat enables, BUT an SCR Signal exists, then show the SCR Signal Mout. However, if there are heat enables, then DO NOT show the SCR Signal Mout option.
| Mout # - Enable | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | none
|  | Not Tested | SCR Enable |  |  | Radio Button | y | PinLocation, point to this MOUT |  |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/isSCR | true | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
|  | Not Tested | Fixed Enable |  |  | Radio Button | y |  |  |  | cfg/i/gc/boards/heating/1/MOUT/5/ehs/isSCR | false | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
| Mout # - SCR Enable | Not Tested | Aux Heat |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/auxHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
|  | Not Tested | Emergency Heat |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/emergencyHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
| Mout # - Fixed Enable | Not Tested | Aux Heat |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/auxHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
|  | Not Tested | Emergency Heat |  |  | Checkbox | n |  |  |  | cfg/i/gc/boards/heating/1/MOUT/1/ehs/emergencyHeat | true | [12 empty] | Gray out if Simultaneous Heat/Cool is DISABLED
| Water/Steam | Not Tested | Min Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/waterMinVolts | {{float}} | [6 empty] | VDC |  |  | 0
|  | Not Tested | Max Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/waterMaxVolts | {{float}} | [6 empty] | VDC |  |  | 10
| Heat Pump Setpoints | Dev and passed testing | Aux Off Delay |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOffTime | {{int}} | [6 empty] | min
|  | Dev and passed testing | Aux On Delay |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOnTime | {{int}} | [6 empty] | min
|  | Dev and passed testing | Aux Off Window |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOffWindow | {{float}} | [6 empty] | F or C
|  | Dev and passed testing | Aux On Window |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/heatPumpConfig.auxOnWindow | {{float}} | [6 empty] | F or C
|  | Not Tested | Heat Pump OAT Lockout |  |  | Setpoint |  |  |  |  | cfg/i/heatPump/minOutdoorAirTemp | {{float}} | [6 empty] | F or C
|  | Not Tested | Heat Superheat Setpoint |  |  | Setpoint | [5 empty] | {{float}}
Gas | Heat Boards | Not Tested | Heat Board 1 Unique ID |  |  | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/1/uuid | {{int}}
|  | Not Tested | Heat Board 2 Unique ID |  |  | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/2/uuid | {{int}}
| Ignition Control Board 1 | Unknown
| Ignition Control Board 1 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/0/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/0/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/0/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/0/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 2 | Unknown
| Ignition Control Board 1 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/1/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/1/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/1/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/1/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 3 | Unknown
| Ignition Control Board 3 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/2/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/2/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/2/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/2/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 4 | Unknown
| Ignition Control Board 4 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/3/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/3/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/3/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/3/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 5 | Unknown
| Ignition Control Board 5 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/4/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/4/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/4/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/4/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 6 | Unknown
| Ignition Control Board 6 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/5/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/5/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/5/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/5/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 7 | Unknown
| Ignition Control Board 7 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/6/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board.
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/6/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/6/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/6/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
| Ignition Control Board 8 | Unknown
| Ignition Control Board 7 | Dev and passed testing | None |  |  | Radio Button | n | FOR ALL Igntion Control Boards: |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | none
|  | Dev and passed testing | Modulating |  |  | Radio Button | y | They are linked to a certain heating board, this is designated in the topic as heating/1 and that part of the topic should change depending on which heating board this ignition controller is being configured from (heat board 1 = 1, heat board 2 = 2 |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | modulating
|  | Dev and passed testing | Fixed |  |  | Radio Button | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/isModulating | fixed
| Modulating - Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/7/modulatingEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/modulatingEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/modulatingEnables | 2
| Modulating - Enables | Can't Test | None |  |  | Radio Button | n | For UI Only
|  | Can't Test | Enables |  |  | Radio Button(s) | y
| Modulating Heat 1 - Mouts | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating Heat 2 - Mouts | Not Tested | None |  |  | Radio Button |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) |  |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Modulating - Low Speed | Not Tested | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | y |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/inducerLowSpeed | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Inducer Fan Low Speed". You cannot select the same Mout again in another ignition control board. Gray out option and throw validation message if they try to select it
| Modulating - Valves | Unknown | ModGas Valves Menu Button |  |  | Menu Button |  | For UI Only | [16 empty] | If on the heating board, there are NO valves enabled, gray out this button
|  | Unknown | Valve 1 |  |  | Menu Button | [18 empty] | Show number of valves enabled on the heating board. If valve 1 configured, show valve 1. If valve 2, show valve 2, if both, both.
|  | Unknown | Valve 2 |  |  | Menu Button | [18 empty] | Show number of valves enabled on heating board. If Valve 2 is not configured, do not show valve 2.
|  | Not Developed | Disable |  |  | Radio Button | n | Number inside the [ ] needs to be replaced with the valve number, 0 based index ( Valve1 => 0, Valve2 => 1 ) |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | false
|  | Not Developed | Enable |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/valveEnabled[0] | true
| Fixed Enables | Dev and failed testing | None |  |  | Radio Button | n | For UI Only | ui/heating/1/ignitionController/7/fixedEnables | none
|  | Dev and failed testing | 1 Enable |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/fixedEnables | 1
|  | Dev and failed testing | 2 Enables |  |  | Radio Button | y |  | ui/heating/1/ignitionController/7/fixedEnables | 2
| Fixed Heat 1 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[0] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Fixed Heat 2 Enables | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | none
|  | Not Tested | Mout (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/heatEnable[1] | {{PinLocation}} | [12 empty] | On the heating board, show only the Mouts selected as "Heat Enable". Also, you cannot select the same Mout again in another area. So if you select Mout 1 on Heat 1, you cannot select it on Heat 2, or any "Heat" on another Ignition Control Board.
| Ignition Proof | Dev and passed testing | None |  |  | Radio Button | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | none
|  | Not Tested | Binary Inputs (PLEASE READ NOTES) |  |  | Radio Button(s) | n |  |  |  | cfg/i/gc/heatConfig/boards/heating/1/ignitionController/7/ignitionProof[0] | {{PinLocation}} | [12 empty] | IF Valve 1 is configured (enabled) please gray out Binary Input 1. If Valve 2 is configured, please gray out Binary Input 2. If disabled, degray. Show only the ones configured for Ignition Proofing
Unknown
Electric | Boards | Unknown | Heat Board 1 |  |  | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/1/uuid | {{int}}
|  | Unknown | Heat Board 2 |  |  | Menu Button |  |  |  |  | cfg/i/gc/boards/heating/2/uuid | {{int}}
| Heat Enable Mouts | Unknown | Mout(s) |  |  | Menu Button(s) | [18 empty] | From Heating board, if there are no heat enables, BUT an SCR Signal exists, then show the SCR Signal Mout. However, if there are heat enables, then DO NOT show the SCR Signal Mout option.
| Mout Enable | Dev and passed testing | None | 1)Payload - field value 2)topics - field value 3)UI Topic and payload added with retain |  | Radio Button | n |  | ui/boards/heating/#/ehs/enable |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/enable | none
|  | Dev and failed testing | SCR Enable | 1)Payload - field value 2)topics - field value 3)UI Topic and payload added with retain |  | Radio Button | n | replace heating/1/MOUT/5 with the pin location of this Mout | ui/boards/heating/#/ehs/enable |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/isSCR | true | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
|  | Dev and failed testing | Fixed Enable | 1)Payload - field value 2)topics - field value 3)UI Topic and payload added with retain |  | Radio Button | n |  | ui/boards/heating/#/ehs/enable |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/isSCR | false | cfg/i/gc/boards/heating/1/MOUT/5/ehs/enable | {{PinLocation}}
| SCR enable | Not Developed | Aux Heat |  |  | Radio Button |  |  |  |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/emergencyHeat | false
|  | Not Developed | Emergency Heat |  |  | Radio Button |  |  |  |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/emergencyHeat | true
| Fixed Enables | Not Developed | Aux Heat |  |  | Radio Button |  |  |  |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/emergencyHeat | false
|  | Not Developed | Emergency Heat |  |  | Radio Button |  |  |  |  | cfg/i/gc/boards/heating/#/MOUT/#/ehs/emergencyHeat | true
Water/Steam | Water/Steam | Dev and failed testing | Min Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/waterMinVolts | {{float}} | [6 empty] | VDC |  |  | 0
|  | Dev and failed testing | Max Voltage |  |  | Setpoint |  |  |  |  | cfg/i/gc/heatConfig/waterMaxVolts | {{float}} | [6 empty] | VDC |  |  | 10

## Cooling
Section | Page |  | Feature | Dev Changes | Type | Chevron? | Topic Notes | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Cooling | Circuit Menu | Dev and passed testing | Circuit A |  | Menu Button |  |  | Just buttons | [13 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit B |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit C |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit D |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit E |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit F |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit G |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
|  | Dev and passed testing | Circuit H |  | Menu Button | [16 empty] | This will populate from the Refrigeration enables section, per board. So, if on Cooling Board 1, you select something other than "none" for refrigeration 1, then you have 1 circuit. If you do the same for refrigeration 2, then you have 2 circuits. This ultimately counts up by the board. So with 4 boards, you can activate 8 refrigerations, meaning you can have up to 8 circuits.
| Setpoints | Dev and passed testing | Stage Up Window |  | Setpoint |  |  | cfg/i/manager/cooling/stageUpWindow
|  | Dev and passed testing | Stage Down Window |  | Setpoint |  |  | cfg/i/manager/cooling/stageDownWindow
|  | Dev and passed testing | Stage Up Timer |  | Setpoint |  |  | cfg/i/manager/cooling/stageUpTime
|  | Dev and passed testing | Stage Down Timer |  | Setpoint |  |  | cfg/i/manager/cooling/stageDownTime
|  | Dev and passed testing | Minimum Run Time |  | Setpoint |  |  | cfg/i/gc/refrigConfig/minRunTimeMinutes
|  | Dev and passed testing | Minimum Off Time |  | Setpoint |  |  | cfg/i/gc/refrigConfig/minOffTimeMinutes
|  | Dev and passed testing | Cooling OAT Lockout |  | Setpoint |  |  | cfg/i/dxCool/oatLockout
|  | Dev and passed testing | Cool SAT Setpoint |  | Setpoint |  |  | sp/i/saTempCoolSP/min
|  | Dev and passed testing | Low SAT Cutoff |  | Setpoint |  |  | cfg/i/supplyAirTempCutoffLow
|  | Dev and passed testing | Cool Min Fan Speed |  | Setpoint |  |  | cfg/i/SZVAV/fanCoolMinSpeed
|  | Dev and passed testing | Cool Control Window |  | Setpoint |  |  | cfg/i/manager/cooling/controlWindow
|  | Dev and passed testing | Cool Superheat Setpoint |  | Setpoint |  |  | cfg/i/superheatSP
|  | Dev and passed testing | Changeover Delay Time |  | Setpoint |  |  | cfg/i/oppositeModeLockoutTime
Circuit A | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitA/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitA/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint | 1)topic - field value | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitA/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitA/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit B | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitB/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitB/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitB/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitB/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit C | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitC/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitC/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitC/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitC/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit D | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitD/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitD/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitD/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitD/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit E | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitE/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitE/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitE/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitE/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit F | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitF/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitF/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitF/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitF/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit G | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitG/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitG/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitG/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitG/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"
Circuit H | Compressor(s) | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/compressors[0] | none
|  | Dev and failed testing | Cooling Board x, Refrigeration x, x Compressor | Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitH/compressors[0] | {{PinLocation}} | [12 empty] | This is dependent on what you pick in the refrigeration enables sectionof the cooling board. you either get the single or tandem compressors.
|  | Dev and failed testing | Tandem Compressor (2) |  | Radio Button | y |  | cfg/i/gc/refrigConfig/circuitH/compressors[1] | {{PinLocation}}
| Compressor 1 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/VICommPort | {{EXVLocation}} | [12 empty] | This is depending on what is selected at the power-comm board level. If Comm 1 is enabled, then you show exv 1, if exv 2 is either indoor or outdoor, then you show EXV 2.
| Compressor 1 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/dischargeLineTempSP | {{float}}
| Compressor 2 - Vapor Injection Comm Port | Not Developed | None | Topic retained | Radio Button | n | This data is on the VFD port {{PinLocation}} the compressor is plugged in to, make sure to update that part of the topic | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | none
|  | Not Developed | Power-Comm Board x, Comm x, EXV x | 1)Payload - field value 2.)Topic retained | Radio Button | y |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/VICommPort | {{EXVLocation}}
| Compressor 2 - Vapor Injection Setpoints | Not Developed | Superheat Setpoint | topic change -to - cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/superheatSP | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/superheatSP | {{float}}
|  | Not Developed | Startup Disable Time | topic changed- to-cfg/i/gc/refrigConfig/cooling/1/VFD/1/compressor/vi/startupDisableTimeMinutes | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/startupDisableTimeMinutes | {{int}}
|  | Not Developed | Discharge Line Temp Setpoint |  | Setpoint |  |  | cfg/i/gc/refrigConfig/cooling/1/VFD/2/compressor/vi/dischargeLineTempSP | {{float}}
| Condenser Fan | Not Developed | AHU Board 1, VFD Port x | Retained | Checkbox | n | The array needs to contain all the selected condenser fans | cfg/i/gc/refrigConfig/circuitH/condenserFans | JSON array of {{PinLocation}}s as strings: [ "airHandler/1/VFD/2", "outsideAir/1/VFD/1" ] | [12 empty] | This uses whatever VFD Ports in the AHU board were configured as "Condenser Fan"
| Inside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/indoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/indoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Inside" on the Power Comm Board
| Outside EXV | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/outdoorEXV | none
|  | Not Developed | Power-Comm Board x, Port x, X EXV # |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/outdoorEXV | {{EXVLocation}} | [12 empty] | Populates based on what EXV's are set as "Outside" on the Power Comm Board
| Reversing Valve | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/reversingValve | none
|  | Not Developed | AHU Board x, Mout X |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/reversingValve | {{PinLocation}} | [12 empty] | Populates based on what Mout on the AHU board is configured as "Reversing Valve"
| Reheat Valve | Dev and failed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/reheatValve | none
|  | Dev and failed testing | Cooling Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
|  | Dev and failed testing | AHU Board x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/reheatValve | {{PinLocation}} | [12 empty] | populate based on how many boards are config'd as either AHU or Cooling Boards
| Proof of Waterflow | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/proofOfWater | none
|  | Not Developed | Cooling Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/proofOfWater | {{PinLocation}} | [12 empty] | Populates based on what Mout on the Cooling board is configured as "Proof of H2O"
|  | Not Developed | AHU Board x, Binary Input x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/proofOfWater | {{PinLocation}}
| Defrost | Not Developed | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/defrostSwitch | none
|  | Not Developed | AHU Board x, Binary Inut x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/defrostSwitch | {{PinLocation}} | [12 empty] | Populates based on what Binary Input on the Cooling board is configured as "Defrost"
| Startup Solenoid | Dev and passed testing | None |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/startupSolenoid | {{PinLocation}}
|  | Not Developed | Cooling Board x, Mout x |  | Radio Button | n |  | cfg/i/gc/refrigConfig/circuitH/startupSolenoid | {{PinLocation}} | [12 empty] | Populates based on what Mout(s) on the cooling board is configured as "startup solenoid"

## Fans
Section | Page | Status | Feature | Type | Chevron? | Dev Changes |  | Topic | Payload | Topic 2 (if required) | Payload 2 (if required) | Topic 3 (if required) | Payload 3 (if required) | Validation Check | Validation Check 2 (if required) | Unit | Min Value | Max Value | Default Value | i-Icon Description | Availability | Notes
Supply Fans | Supply Fan Config | Dev and passed testing | CAV | Radio Button | n |  |  | cfg/i/manager/supplyFan/controlMode | CAV
|  | Dev and passed testing | Filter Loading | Child Checkbox | y |  |  | cfg/i/supplyFan/filterLoading | true
|  | Dev and passed testing | SZVAV | Radio Button | y |  |  | cfg/i/manager/supplyFan/controlMode | Sequence
|  | Dev and passed testing | Building Pressure | Radio Button | y |  |  | cfg/i/manager/supplyFan/controlMode | ModBuildingPressure | [12 empty] | Chevron goes to bldg pr workflow
|  | Not Tested | Controls Min OA | Radio Button | y |  |  | cfg/i/manager/supplyFan/controlMode | ControlsMinOA
|  | Dev and passed testing | Duct Static Control | Radio Button | y |  |  | cfg/i/manager/supplyFan/controlMode | ModStaticPressure
|  | Dev and passed testing | Has Static Reset | Child Checkbox | y |  |  | cfg/i/manager/ductStaticControl/staticReset/enable | true
|  | Dev and failed testing | Supply Fan Cycles w/ Heat/Cool | Checkbox | n | Retained | The logic on this point is reversed from the way it is written in the UI. Fan cycling would be occRunFan = false, and default behavior would be true | cfg/i/occRunFan | boolean |  |  |  |  | Unit MUST be in standard mode
|  | Dev and failed testing | SF runs while Unoccupied | Checkbox | y | Retained |  | cfg/i/unoccRunFan | boolean | [12 empty] | Gray out the chevron button if Duct Static Pressure is selected
| Filter Loading SP's | Dev and passed testing | Duct Static Setpoint | Setpoint |  |  |  | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the supply fan. The supply fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and passed testing | Duct Static Deadband | Setpoint |  |  |  | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.1 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
| SZVAV Setpoints | Dev and passed testing | Heat Min VFD | Setpoint |  |  |  | cfg/i/SZVAV/fanHeatMinSpeed | integer | [6 empty] | % | 0 | 100
|  | Dev and passed testing | Heat Max VFD | Setpoint |  |  |  | cfg/i/SZVAV/fanHeatMaxSpeed | integer | [6 empty] | % | 0 | 100
|  | Dev and passed testing | Cool Min VFD | Setpoint |  |  |  | cfg/i/SZVAV/fanCoolMinSpeed | integer | [6 empty] | % | 0 | 100
| Duct Static SP's | Dev and passed testing | Duct Static Setpoint | Setpoint |  |  |  | sp/i/ductStaticPressureSP | float | [6 empty] | "WG | 0.1 | 3 | 1.5 | Enter the desired pressure to be maintained by the supply fan. The supply fan VFD speed will increase as the actual duct static pressure drops below this value and will decrease as the actual duct static pressure rises above this value.
|  | Dev and passed testing | Duct Static Deadband | Setpoint |  |  |  | sp/i/ductStaticPressureDB | float | [6 empty] | "WG | 0.01 | 0.5 | 0.1 | Enter the acceptable tolerance from setpoint the duct static shall be allowed to remain without making fan speed adjustments.
| Static Reset SP's | Dev and passed testing | Minimum | Setpoint |  |  |  | cfg/i/manager/ductStaticControl/staticReset/min | [7 empty] | % | 0 | 100
| Global SF Setpoints | Dev and passed testing | Cool Min Speed | Setpoint |  | Retained |  | cfg/i/SZVAV/fanCoolMinSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | Vent Speed | Setpoint |  | Retained |  | cfg/i/SZVAV/fanVentMinSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | Heat Min Speed | Setpoint |  | Retained |  | cfg/i/SZVAV/fanHeatMinSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | Heat Max Speed | Setpoint |  | Retained |  | cfg/i/SZVAV/fanHeatMaxSpeed | [7 empty] | % | 0 | 100
|  | Dev and passed testing | # of Allowed Fan Failures | Setpoint |  | Retained | We're missing this setpoint for return and exhaust fans | cfg/i/gc/fanConfig/numAllowedSupplyFanFailures | integer
| SF During Unoccupied Mode | Dev and passed testing | Fixed Speed | Setpoint |  |  |  | cfg/i/SZVAV/fanUnocc/fixedSpeed | integer | [6 empty] | % | 0 | 100
Return Fan | Config | Can't Test | CAV (Default) | Radio Button | n |  |  | cfg/i/pressureRelief | ReturnCAV
|  | Can't Test | Building Pressure Control | Radio Button | y |  |  | cfg/i/pressureRelief | ReturnFanBuildingPressure | [12 empty] | Navigates to Building Pressure workflow
| Allowed Fails | Can't Test | Number of allowed fan failures | Setpoint |  |  |  | cfg/i/gc/fanConfig/numAllowedReturnFanFailures
Exhaust Fan | Config | Can't Test | CAV (Default) | Radio Button | n |  |  | cfg/i/pressureRelief | ExhaustCAV
|  | Can't Test | Building Pressure Control | Radio Button | y |  |  | cfg/i/pressureRelief | ExhaustFanBuildingPressure | [12 empty] | Navigates to Building Pressure workflow
| Allowed Fails | Can't Test | Number of allowed fan failures | Setpoint |  |  |  | cfg/i/gc/fanConfig/numAllowedReturnFanFailures

## Board Config Options
| All basic board selections can be made via |  |  | In the case of disable/enable, set the pin to none or the appropriate value
| cfg/i/gc/boards/{BoardName}/{BoardNumber}/{PinType}/{PinNumber}/selection |  |  | I think I got everything in here, but I may have missed some, let me know if something is missing
Example, AirHandler board 1, MOUT 2 is now reversingValve
| Topic: |  | Payload
| cfg/i/gc/boards/airHandler/1/MOUT/2/selection |  | reversingValve
PinName | AIN | BIN | MOUT | DamperConnection | EXVComm | ReheatValve | ModGasValve | A2L | BoardNames (might change? Will finalize by 3/21)
| none | none | none | none | none | none | none | none | cooling
| preheatEnteringAirTemp | 24VPowerAlert | heatEnable | oaDamper | sporlanEXV | reheatValve | modGasValve | cabinet | airHandler
| preheatLeavingAirTemp | PBOAlert | scrSignal | raDamper | sporlanEXV_VI |  |  | airstream | preheat
| oaTemp | powerSupplyThermalAlert | reversingValve | motorizedExhaustDamper | sanhuaEXV |  |  |  | modHeat
| raTemp | supplyAirflowSwitch | morningWarmup/cooldown | rabDamper |  |  |  |  | heatWheel
| buildingPressure | returnAirflowSwitch | lowAmbientEnable | ervDamper |  |  |  |  | powerComm
| exhaustDuctStaticPressure | exhaustAirflowSwitch | returnFanEnable | [5 empty] | outsideAir
| ductStaticPressure | dirtyFilterSwitch | exhaustFanEnable
| saTemp | dirtyPreFilterSwitch | supplyFanEnable
| spaceTemp | hoodOn | econoActive
| spaceSlideAdjust | remoteShutdown | occupiedActive
| analogOilLevelSensor | remoteOccupied | overrideActive
| erIntakeLeavingAirTemp | proofOfH20 | alarmActive
| erExhaustLeavingAirTemp | defrostSwitch | reheatActive
| BACnetPassthrough | ignitionProof | coolEnable
|  | oilLevelSwitch | preheatEnable
|  | intakeFilterSwitch | inducerFanLowSpeed
|  | exhaustFilterSwitch | unloader
|  | rotationStatus | compressorEnable(step)
|  | BACnetPassthrough | startupSolenoid
heatWheelEnable
|  | heatLimitSwitch | heatWheelLowSpeed
|  | preheatLimitSwitch | bypassDamperEnable
condenserFanEnable
BACnetPassthrough
| Pin Location Payload Format | {{PinLocation}} gets replaced with the following
BoardType/BoardNum/PinType/PinNumber
heating/1/MOUT/3
airHandller/2/BIN/1
| none | Special option to clear out any previous data for this location
| EXVLocation Payload Format | {{EXVLocation}} gets replaced with the following
| {{PinLocation}}/1 | EXV1 plugged in to {{PinLocation}}
or
| {{PinLocation}}/2 | EXV2 plugged in to {{PinLocation}}
| powerComm/1/exvComm/3/2 | On powerComm board 1, commPort 3, exv 2 of the compound controller
| {{Pin Location}} | BoardType/BoardNum/PinType/PinNumber | BoardType | BoardNum | PinType | definition | PinNumber
|  |  | cooling | 0-6 | AIN | Analog Input | 0-12
|  |  | airHandler |  | BIN | Binary Input
|  |  | preheat |  | MOUT | MOUT
|  |  | modHeat |  | DamperConnection | Damper Port
|  |  | heatWheel |  | EXVComm | EXV
|  |  | powerComm |  | ReheatValve | Reheat Valve
|  |  | outsideAir |  | ModGasValve | Mod Gas
|  |  | heating |  | A2L | A2L
| {{EXVLocation}} | powerComm/BoardNum/exvComm/CommNum/EXVNum | BoardNum | CommNum | EXVNum
|  |  | 0-6 | 0-6 | 0-2
Examples
| heating/1/MOUT/3 | heating = board type, 1 = heat board 1, MOUT = pin type, 3 = pin number
| airHandler/2/BIN/1 | airHandler = board type, 2 = ahu board 2, BIN = pin type, 1 = pin number
| none | Special option to clear out any previous data for this location
| powerComm/1/exvComm/3/2 | powerComm = constant, 1 = boardNum, exvComm = constant, 3 = CommNum, 2 = EXV Num
| none | Special option to clear out any previous data for this location